## Instructions
TOLERANCE SURVEY LOG — Instructions
WHAT THIS WORKBOOK IS
Daily survey + deviation log for AISC §7.13 tolerance compliance. Pair with the Plumb-and-True Tolerance Guide HTML. The workbook auto-flags OK / Out-of-Tolerance based on §7.13 limits.
WORKFLOW
1. Project Info: project, GC, erector, surveyor, EOR, project-spec tolerance (default §7.13 OR tighter per Contract).
2. Anchor Rod Survey: log every anchor — theoretical and as-found positions. Variance auto-computes. Out-of-tolerance items auto-flag.
3. Column Plumb Log: log every column at every plumb-up event (initial, bay plumb-up, top-out). Enter offset at top of column in X and Y from theoretical plumb. Compare to 1:500 limit (or project-specific limit).
4. Floor Elevation Log: log beam-top elevations vs theoretical. Multi-point per floor (typically 4 corners + center).
5. Deviation / RFI Tracker: any out-of-tolerance item that requires EOR review gets a row here. Track RFI #, EOR response, resolution, re-survey confirmation.
6. Daily Survey Summary: auto-totals — surveys completed today, deviations open, RFIs pending.
AISC §7.13 KEY LIMITS (built into the workbook)
Column plumb: 1:500 of column length (with per-length table on Tolerance Reference tab)
Anchor rod position (single): ±1/8"
Anchor rod pattern position: ±1/4"
Anchor rod stickup: ±1/8"
Beam top elevation: ±1/8"
Floor-to-floor height: ±1/4"
TIGHTER PROJECT-SPEC TOLERANCES
If the Contract Documents specify tighter tolerances (AESS, hospital, MRI, etc.), override the default on Project Info. The workbook will apply the tighter limit when flagging out-of-tolerance items.
SURVEY EVENT TYPES
- Initial: column just set, before next beam frames to it
- Bay plumb-up: after 2-bay placement, before next bays
- Top-out: after last column set on this elevation
- Pre-cladding: as-built before curtainwall sub mobilizes
- Final / Substantial Completion: archive record
DEVIATION RESOLUTION
Any out-of-tolerance column is either (a) re-plumbed via diagonal bracing (if column still adjustable) and re-surveyed, OR (b) RFI'd to EOR. The Deviation Tracker handles both paths.
AS-BUILT SIGN-OFF
At Substantial Completion, the workbook (plus the EOR's acceptance letter) is the evidence file for the cladding mobilization gate and the retainage reduction request.

## Project Info
TOLERANCE SURVEY — PROJECT INFO
Project Name
Project Address
Owner
Controlling Contractor (GC)
Steel Erector
EOR (Structural Engineer of Record)
Surveyor (in-house or sub)
Total Station Make / Model
Total Station Calibration Date
Benchmark Reference Monument 1 (location)
Benchmark Reference Monument 2 (location)
PROJECT-SPEC TOLERANCE OVERRIDES (leave default = §7.13 if not tightened)
Column plumb ratio (default 500 → 1:500) | 500
Anchor rod single position tolerance (in) | 0.125
Anchor rod pattern position tolerance (in) | 0.25
Anchor rod stickup tolerance (in) | 0.125
Beam top elevation tolerance (in) | 0.125
Floor-to-floor height tolerance (in) | 0.25
Exterior column drift envelope (in, at corners) | 1

## Anchor Rod Survey
ANCHOR ROD SURVEY
Pre-erection verification of anchor rods. ΔX/ΔY are computed in inches; radial deviation is the absolute distance from theoretical. Single-Rod tolerance default = ±1/8" (per AISC §7.5.1).
Column ID | Anchor Rod # | Theo X (ft) | Theo Y (ft) | As-Found X (ft) | As-Found Y (ft) | ΔX (in) | ΔY (in) | Radial Dev (in) | Theo Stickup (in) | As-Found Stickup (in) | Stickup Dev (in) | Single-Rod Position OK? | Stickup OK? | Notes / RFI

## Column Plumb Log
COLUMN PLUMB LOG
Offsets measured at top of column from theoretical plumb vertical. Column Length is from top of base plate to top of column (or to top of splice on multi-story). Allowable = ColumnLength * 12 / PlumbRatio (default 1:500).
Survey Date | Event Type | Column ID | Gridline | Column Length (ft) | Offset X at Top (in) | Offset Y at Top (in) | Total Radial Dev (in) | Allowable (1:Ratio of length, in) | Plumb OK? | Surveyor | Adjusted Y/N | Re-Survey Date | Notes / RFI

## Floor Elevation Log
FLOOR / BEAM ELEVATION LOG
Beam-top elevations per floor. Recommended survey points: each corner + center. Theoretical from S-series drawings. Deviation auto-flags against ±1/8" beam-top tolerance (default §7.13.1.4).
Survey Date | Floor Level | Survey Point ID | Location | Theo Elevation (ft) | As-Found Elevation (ft) | Deviation (in) | Beam Top OK? | Adjacent Beam Match (in) | Beam Match OK? | Surveyor | Notes / RFI

## Deviation RFI Tracker
DEVIATION / RFI TRACKER
One row per out-of-tolerance item requiring EOR review. Tracks the RFI through to resolution.
Dev # | Discovered Date | Survey Reference | Item Type | Location / Column ID | Description | Measured | Allowable | RFI # | Sent to EOR (Date) | EOR Response Date | EOR Disposition | Resolution Date | Resolved Status | Notes

## Daily Summary
DAILY SURVEY SUMMARY
Auto-aggregated. Use for monthly billing back-up + as-built sign-off package.
ANCHOR ROD SURVEY
Total anchor rods surveyed
Anchor rods position OK
Anchor rods position OUT
Anchor rods stickup OK
Anchor rods stickup OUT
COLUMN PLUMB
Total plumb surveys
Columns plumb OK
Columns plumb OUT
FLOOR ELEVATION
Total elevation surveys
Beam top OK
Beam top OUT
DEVIATION TRACKER
Total deviations logged
Deviations Open
Deviations RFI Sent
Deviations EOR Review
Deviations Resolved + Closed
READINESS FOR CLADDING / RETAINAGE
Open deviations blocking sign-off

## Tolerance Reference (hidden)
AISC §7.13 — Tolerance Limits Reference
Item | Default Limit | AISC §
Anchor rod single position | ±0.125" (1/8") | §7.5.1
Anchor rod pattern position | ±0.250" (1/4") | §7.5.1
Anchor rod stickup | ±0.125" (1/8") | §7.5.2
Anchor rod plumb (vertical) | 1:40 | §7.5.2
Column plumb | 1:500 of length | §7.13.1.2
Beam top elevation | ±0.125" (1/8") | §7.13.1.4
Floor-to-floor height | ±0.250" (1/4") | §7.13.1.4
Building drift (multi-story) | 1:500 from base, exterior columns | §7.13.1.3
Member straightness (mill) | Per ASTM A6 | ASTM A6
Member camber preservation | Per shop drawings | Project spec