## Instructions
ELECTRICAL BID ESTIMATOR — INSTRUCTIONS
PURPOSE
Production estimating tool for commercial electrical contractors. Uses NECA Labor
Units (per device + per LF of conduit + per termination). CSI Division 26 primary
with cross-references to 27 (communications) and 28 (electronic safety + security).
Output rolls up by CSI division so the bid integrates cleanly into the GC's job-cost
accounting + into your monthly billing on the Universal Sub Suite's
Sub_Schedule_of_Values.xlsx.
WORKFLOW
1. Project Info — fill every blue field.
2. Wage Rates — set base + fringe + OT premium by classification.
3. Material Takeoff — quantities by CSI line item (conduit type+size, wire AWG,
device class, gear). Unit costs flow into Bid Summary.
4. Labor Estimate — NECA Labor Units assume average commercial conditions.
Adjust productivity factor for difficult work.
5. Equipment — daily/weekly rentals (lifts, generator, bender, knockout sets).
6. Subcontract — fire alarm certification, low-voltage, gear assembly + factory test.
7. Premiums — height, hazardous, prevailing wage, occupied-building disruption.
8. Bid Summary — automatic roll-up + final bid number.
NECA LABOR UNITS
Hours-per-unit values approximate published NECA Labor Units for standard commercial
work. Confirm against your jurisdiction + the latest NECA edition. Calibrate against
your historical productivity. Underestimating labor is the #1 cause of electrical-
bid losses; if your historical productivity differs from these defaults by more than
15%, change the defaults — don't ignore the gap.
FIELD-ONLY SCOPE
Calibrated for field installation. Switchgear assembly + factory acceptance testing,
specialty fabricated bus assemblies, and modular substation work are typically
subbed and entered on the Subcontract tab.
DOCUMENT VERSION
Electrical_Bid_Estimator.xlsx v1.0 — 2026-05-19
ContrPro Complete Tier · Electrical Trade Pack

## Bid Summary
BID SUMMARY — Electrical Trade Pack
Material total (incl. tax)
Labor total
Equipment total
Subcontract total
Premiums $
Direct cost subtotal
Premium % applied
Premium % adder $
Direct + premium %
| Contingency % | 5%
Contingency $
Direct + contingency
| Overhead % | 10%
Overhead $
| Profit % | 10%
Profit $
| Bond % | 1.2%
Bond $
| Insurance / GL % | 1.8%
Insurance $
FINAL BID

## Project Info
PROJECT INFORMATION
Project Name
Project Address
Owner
General Contractor
Architect / Engineer
Bid Due Date
Bid Reference / Number
Project Type | (New construction / Renovation / Tenant fit-out / Adaptive reuse)
Building Use | (Office / Retail / Healthcare / Education / Multi-family / Hospitality / Industrial / Mixed)
Approx. Square Footage
Stories
Service Size (Amps / Volts / Phase)
AHJ — Electrical Inspector
Applicable NEC Edition | (NEC 2023 + local amendments)
Estimator Name
Estimator Phone
Estimator Email
Date Prepared
Internal Bid Number
Notes / Assumptions

## Wage Rates
WAGE RATES (calibrate to your market)
Classification | Base Rate ($/hr) | Fringe ($/hr) | Burden % (WC/GL/FICA) | OT Premium (1.5×) | Loaded Rate ($/hr)
Electrical Foreman | 62 | 19.5 | 32%
Journeyman Electrician | 52 | 19.5 | 32%
Apprentice (Yr 4) | 40 | 14.5 | 32%
Apprentice (Yr 2) | 28 | 12 | 32%
Material Handler / Helper | 22 | 9.5 | 32%
Low-Voltage Tech | 48 | 17 | 32%
Fire Alarm Certified Tech | 58 | 19 | 32%

## Material Takeoff
MATERIAL TAKEOFF (CSI Division 26)
CSI Code | Description | QTY | UOM | Unit Cost ($) | Material Subtotal ($) | Notes
26 05 19 | Conductor — THHN/THWN-2, #14 AWG copper | 0 | LF | 0.18
26 05 19 | Conductor — THHN/THWN-2, #12 AWG copper | 0 | LF | 0.28
26 05 19 | Conductor — THHN/THWN-2, #10 AWG copper | 0 | LF | 0.48
26 05 19 | Conductor — THHN/THWN-2, #8 AWG copper | 0 | LF | 0.85
26 05 19 | Conductor — THHN/THWN-2, #6 AWG copper | 0 | LF | 1.45
26 05 19 | Conductor — THHN/THWN-2, #4 AWG copper | 0 | LF | 2.4
26 05 19 | Conductor — THHN/THWN-2, #2 AWG copper | 0 | LF | 3.85
26 05 19 | Conductor — THHN/THWN-2, 1/0 AWG copper | 0 | LF | 6.5
26 05 19 | Conductor — THHN/THWN-2, 2/0 AWG copper | 0 | LF | 8.4
26 05 19 | Conductor — THHN/THWN-2, 4/0 AWG copper | 0 | LF | 13.25
26 05 19 | Conductor — THHN/THWN-2, 250 MCM copper | 0 | LF | 15.75
26 05 19 | Conductor — THHN/THWN-2, 500 MCM copper | 0 | LF | 28
26 05 19 | Conductor — XHHW-2 aluminum, #6 AWG | 0 | LF | 0.85
26 05 19 | Conductor — XHHW-2 aluminum, 250 MCM | 0 | LF | 5.95
26 05 19 | Conductor — XHHW-2 aluminum, 500 MCM | 0 | LF | 11.5
26 05 26 | Ground rod — 5/8" × 8' copper | 0 | EA | 14.5
26 05 26 | Ground rod — 5/8" × 10' copper | 0 | EA | 21.5
26 05 26 | Ground clamp — acorn | 0 | EA | 3.85
26 05 26 | Bare copper bond — #6 AWG | 0 | LF | 1.2
26 05 26 | Bare copper bond — #4 AWG | 0 | LF | 1.85
26 05 26 | Bare copper bond — 2/0 AWG | 0 | LF | 7.95
26 05 29 | Unistrut B-line 12 ga, 10' length | 0 | EA | 18.5
26 05 29 | Conduit clamp + spring nut | 0 | EA | 1.85
26 05 29 | Threaded rod 3/8" × 6' | 0 | EA | 6.5
26 05 33 | EMT conduit — 1/2" | 0 | LF | 0.65
26 05 33 | EMT conduit — 3/4" | 0 | LF | 0.95
26 05 33 | EMT conduit — 1" | 0 | LF | 1.45
26 05 33 | EMT conduit — 1-1/2" | 0 | LF | 2.65
26 05 33 | EMT conduit — 2" | 0 | LF | 3.85
26 05 33 | EMT conduit — 3" | 0 | LF | 7.85
26 05 33 | EMT conduit — 4" | 0 | LF | 11.5
26 05 33 | Rigid steel conduit — 1" | 0 | LF | 5.85
26 05 33 | Rigid steel conduit — 2" | 0 | LF | 12.5
26 05 33 | PVC schedule 40 — 3/4" | 0 | LF | 0.55
26 05 33 | PVC schedule 40 — 1" | 0 | LF | 0.85
26 05 33 | PVC schedule 40 — 2" | 0 | LF | 2.2
26 05 33 | PVC schedule 40 — 4" | 0 | LF | 6.5
26 05 33 | MC cable — 12/2 with ground | 0 | LF | 0.85
26 05 33 | MC cable — 12/3 with ground | 0 | LF | 1.15
26 05 33 | Flex conduit — 1/2" Greenfield | 0 | LF | 1.2
26 05 33 | Liquidtight flex — 3/4" | 0 | LF | 4.85
26 05 33 | 4-S box — galvanized | 0 | EA | 4.85
26 05 33 | Single gang box — handy box | 0 | EA | 2.85
26 05 33 | Plaster ring — single gang | 0 | EA | 1.45
26 05 33 | Plaster ring — 2-gang | 0 | EA | 2.2
26 05 33 | PVC adapter — male, 3/4" | 0 | EA | 0.85
26 05 33 | EMT set-screw connector — 1/2" | 0 | EA | 0.55
26 24 16 | Panelboard — 200A, 42-circuit, MLO | 0 | EA | 1685
26 24 16 | Panelboard — 400A, 84-circuit MCB | 0 | EA | 3850
26 24 16 | Panelboard — 800A, MCB + sub-feed | 0 | EA | 7250
26 24 13 | Switchboard — 1200A service entrance | 0 | EA | 18500
26 24 13 | Switchboard — 2500A main | 0 | EA | 38500
26 24 19 | MCC bucket — combination starter | 0 | EA | 1850
26 27 13 | Service entrance — 200A residential | 0 | EA | 1450
26 27 13 | CT cabinet — 800A | 0 | EA | 3850
26 27 13 | Meter base — 200A self-contained | 0 | EA | 285
26 28 16 | Safety switch — 60A fused 600V | 0 | EA | 145
26 28 16 | Safety switch — 200A non-fused 600V | 0 | EA | 485
26 28 16 | Safety switch — 400A fused | 0 | EA | 985
26 28 18 | Circuit breaker — 20A 1P | 0 | EA | 12.5
26 28 18 | Circuit breaker — 50A 2P | 0 | EA | 38.5
26 28 18 | Circuit breaker — 100A 3P | 0 | EA | 145
26 28 18 | Circuit breaker — 400A 3P | 0 | EA | 1485
26 29 13 | Motor starter — size 0 | 0 | EA | 285
26 29 13 | Motor starter — size 2 | 0 | EA | 485
26 29 23 | Variable frequency drive — 5 HP | 0 | EA | 685
26 29 23 | Variable frequency drive — 25 HP | 0 | EA | 2450
26 32 13 | Standby generator — 50 kW diesel | 0 | EA | 28500 |  | Confirm scope split
26 36 23 | Automatic transfer switch — 200A | 0 | EA | 4850
26 41 13 | Air terminal + base | 0 | EA | 38.5
26 41 16 | Down conductor — copper braid | 0 | LF | 4.85
26 51 13 | LED 2x4 troffer — 40W | 0 | EA | 145
26 51 13 | LED 2x2 troffer — 25W | 0 | EA | 115
26 51 13 | LED high-bay — 150W warehouse | 0 | EA | 185
26 51 13 | LED downlight — 6" can | 0 | EA | 65
26 51 13 | Linear LED strip — 4' | 0 | EA | 95
26 51 13 | Wall sconce — LED | 0 | EA | 145
26 51 13 | Occupancy sensor — wall switch | 0 | EA | 45
26 51 13 | Occupancy sensor — ceiling-mount PIR | 0 | EA | 78
26 51 13 | Daylight sensor | 0 | EA | 145
26 51 13 | Emergency battery pack — 90 min | 0 | EA | 285
26 51 13 | Exit sign — LED w/ battery | 0 | EA | 95
26 52 13 | Wall pack — LED 40W full cutoff | 0 | EA | 145
26 52 13 | Pole-mount LED — 150W shoebox | 0 | EA | 685
26 52 13 | Bollard light — LED 15W | 0 | EA | 285
26 27 26 | Receptacle — 20A duplex, decora | 0 | EA | 4.85
26 27 26 | Receptacle — 20A GFCI | 0 | EA | 18.5
26 27 26 | Receptacle — 30A 250V | 0 | EA | 32
26 27 26 | Receptacle — 50A 250V dryer/range | 0 | EA | 38
26 27 26 | Switch — 20A single-pole | 0 | EA | 3.85
26 27 26 | Switch — 20A 3-way | 0 | EA | 6.5
26 27 26 | Switch — 20A 4-way | 0 | EA | 18.5
26 27 26 | Dimmer — 0-10V LED-rated | 0 | EA | 38
26 27 26 | Wallplate — single gang | 0 | EA | 1.45
26 27 73 | Floor box — flush 6-gang | 0 | EA | 285
26 27 73 | Poke-thru floor box | 0 | EA | 485
27 11 13 | Cat 6A cable | 0 | LF | 0.85 |  | If in EC scope
27 11 13 | Cat 6A RJ-45 jack + faceplate | 0 | EA | 14.5
27 13 23 | Fiber multimode 12-strand OM4 | 0 | LF | 4.85
26 00 10 | Permit — electrical | 0 | LS | 0 |  | Allowance — AHJ amount
26 00 10 | Inspection re-trip allowance | 0 | LS | 0
Material Subtotal
|  |  |  | Sales tax % | 7%
Sales tax $
Material TOTAL (incl tax)

## Labor Estimate
LABOR ESTIMATE (NECA Labor Units)
CSI Code | Activity | QTY | UOM | Hours / UOM | Subtotal Hours | Crew Loaded Rate ($/hr) | Subtotal Labor ($)
26 05 33 | Install EMT 1/2" - 3/4" exposed | 0 | LF | 0.045 |  | 70
26 05 33 | Install EMT 1" - 1-1/4" exposed | 0 | LF | 0.06 |  | 70
26 05 33 | Install EMT 2" - 3" exposed | 0 | LF | 0.09 |  | 70
26 05 33 | Install EMT 4" exposed | 0 | LF | 0.13 |  | 70
26 05 33 | Install EMT 1/2" - 1" concealed | 0 | LF | 0.055 |  | 70
26 05 33 | Install rigid steel 1" - 2" | 0 | LF | 0.11 |  | 70
26 05 33 | Install rigid steel 3" - 4" | 0 | LF | 0.18 |  | 70
26 05 33 | Install PVC schedule 40 1" - 2" | 0 | LF | 0.04 |  | 70
26 05 33 | Install PVC schedule 40 3" - 4" | 0 | LF | 0.075 |  | 70
26 05 33 | Install MC cable per LF | 0 | LF | 0.025 |  | 70
26 05 33 | Install liquidtight flex | 0 | LF | 0.075 |  | 70
26 05 19 | Pull #14 - #10 AWG, 3-conductor | 0 | LF | 0.012 |  | 70
26 05 19 | Pull #8 - #4 AWG, 3-conductor | 0 | LF | 0.025 |  | 70
26 05 19 | Pull #2 AWG - 1/0, 3-conductor | 0 | LF | 0.045 |  | 70
26 05 19 | Pull 2/0 - 250 MCM, 3-conductor | 0 | LF | 0.075 |  | 70
26 05 19 | Pull 500 MCM, 3-conductor | 0 | LF | 0.15 |  | 70
26 05 19 | Terminate #14 - #10 AWG | 0 | EA | 0.1 |  | 70
26 05 19 | Terminate #8 - #4 AWG (lug) | 0 | EA | 0.2 |  | 70
26 05 19 | Terminate #2 - 1/0 AWG (lug) | 0 | EA | 0.3 |  | 70
26 05 19 | Terminate 2/0 - 250 MCM (compression) | 0 | EA | 0.5 |  | 70
26 05 19 | Terminate 500 MCM (compression) | 0 | EA | 0.75 |  | 70
26 05 33 | Install 4-S box exposed | 0 | EA | 0.2 |  | 70
26 05 33 | Install handy box + plate exposed | 0 | EA | 0.15 |  | 70
26 05 33 | Install device box concealed (rough-in) | 0 | EA | 0.18 |  | 70
26 27 26 | Set + connect receptacle 20A | 0 | EA | 0.2 |  | 70
26 27 26 | Set + connect GFCI receptacle | 0 | EA | 0.3 |  | 70
26 27 26 | Set + connect single-pole switch | 0 | EA | 0.18 |  | 70
26 27 26 | Set + connect 3-way switch | 0 | EA | 0.3 |  | 70
26 27 26 | Set + connect dimmer (0-10V) | 0 | EA | 0.35 |  | 70
26 27 26 | Set + connect 30A receptacle | 0 | EA | 0.45 |  | 70
26 51 13 | Hang LED 2x4 troffer + connect | 0 | EA | 0.85 |  | 70
26 51 13 | Hang LED 2x2 troffer + connect | 0 | EA | 0.7 |  | 70
26 51 13 | Hang LED high-bay (lift) | 0 | EA | 1.5 |  | 70
26 51 13 | Install LED downlight 6" | 0 | EA | 0.6 |  | 70
26 51 13 | Install wall sconce | 0 | EA | 0.55 |  | 70
26 51 13 | Install occupancy sensor wall | 0 | EA | 0.35 |  | 70
26 51 13 | Install occupancy sensor ceiling | 0 | EA | 0.6 |  | 70
26 51 13 | Install emergency battery pack | 0 | EA | 0.6 |  | 70
26 51 13 | Install exit sign | 0 | EA | 0.5 |  | 70
26 52 13 | Install wall-pack exterior | 0 | EA | 0.75 |  | 70
26 52 13 | Install pole-mount fixture + arm | 0 | EA | 3.5 |  | 70
26 24 16 | Set + connect 200A panelboard | 0 | EA | 4.5 |  | 70
26 24 16 | Set + connect 400A panelboard | 0 | EA | 6.5 |  | 70
26 24 16 | Set + connect 800A panelboard | 0 | EA | 10.5 |  | 70
26 24 13 | Set + connect 1200A switchboard (rig + connect) | 0 | EA | 24 |  | 70
26 27 13 | Set + connect 200A service entrance | 0 | EA | 6 |  | 70
26 28 16 | Set + connect 60A-200A safety switch | 0 | EA | 1.2 |  | 70
26 28 16 | Set + connect 400A safety switch | 0 | EA | 2.5 |  | 70
26 05 26 | Drive ground rod + bond | 0 | EA | 0.45 |  | 70
26 05 26 | Install ground bar in panel | 0 | EA | 0.65 |  | 70
26 05 26 | Run bare copper bond + terminate | 0 | LF | 0.025 |  | 70
26 05 26 | Cad-weld bond connection | 0 | EA | 0.85 |  | 70
27 11 13 | Pull Cat 6A cable + terminate jack | 0 | EA | 0.4 |  | 65
27 13 23 | Pull fiber 12-strand multimode + terminate | 0 | EA | 6 |  | 75
26 08 00 | Megger test feeder (1 hour minimum) | 0 | LS | 1.5 |  | 70
26 08 00 | Ground resistance test (3-point fall-of-potential) | 0 | LS | 2 |  | 70
26 08 00 | Acceptance test — panel/breaker exercise | 0 | EA | 0.5 |  | 70
[6 empty] | Productivity factor | 1
Labor Subtotal

## Equipment
EQUIPMENT ESTIMATE
Equipment | Days | Daily Rate ($) | Weeks | Weekly Rate ($) | Subtotal ($)
Scissor lift — 19' | 0 | 145 | 0 | 485
Boom lift — 45' | 0 | 425 | 0 | 1485
Conduit bender — mechanical 1"-2" | 0 | 65 | 0 | 195
Conduit bender — hydraulic 2-1/2"-4" | 0 | 185 | 0 | 685
Knockout set (1/2"-2") | 0 | 45 | 0 | 135
Knockout set — hydraulic 2-1/2"-4" | 0 | 145 | 0 | 485
Wire-pulling equipment (tugger) | 0 | 165 | 0 | 545
Megger / insulation tester | 0 | 55 | 0 | 165
Ground resistance tester (3-point) | 0 | 95 | 0 | 285
Fluke 87V / 1587 multimeter | 0 | 35 | 0 | 105
Hot-stick set | 0 | 95 | 0 | 285
Arc-flash PPE (Cat 2-4) per worker / week | 0 | 0 | 0 | 145
Voltage detector / proximity meter | 0 | 25 | 0 | 75
Trencher — walk-behind | 0 | 285 | 0 | 1185
Concrete saw + core drill | 0 | 145 | 0 | 525
Fiber fusion splicer | 0 | 285 | 0 | 1185
Cat 6 cable tester (Fluke DSX) | 0 | 145 | 0 | 485
Generator — 5kW portable | 0 | 65 | 0 | 195
Office trailer (allocation) | 0 | 0 | 0 | 285
Truck / van allocation | 0 | 0 | 0 | 425
Equipment Subtotal

## Subcontract
SUBCONTRACT ESTIMATE
Scope (if subbed) | Vendor / Quote | Quote $ | Markup % | Subtotal ($)
Fire-alarm cert + commissioning |  | 0 | 10%
Switchgear assembly + factory test |  | 0 | 10%
Generator startup + commissioning |  | 0 | 10%
ATS commissioning |  | 0 | 10%
Low-voltage cabling (if subbed) |  | 0 | 10%
Security system installation |  | 0 | 10%
Access-control install + commissioning |  | 0 | 10%
Audio-visual install |  | 0 | 10%
Excavation / boring (deep raceway) |  | 0 | 10%
Specialty grounding (counterpoise/MGB) |  | 0 | 10%
Arc-flash study (engineered) |  | 0 | 10%
Concrete saw-cutting / core drilling |  | 0 | 10%
Acceptance testing (NETA cert) |  | 0 | 10%
Subcontract Subtotal

## Premiums
PREMIUMS & CONDITIONS
Premium | Applies? (Y/N) | Adder % | Adder $ (overrides %)
Prevailing wage (Davis-Bacon or state) | N | 15% | 0
Occupied building / live-rewire | N | 12% | 0
Hazardous (Class I Div 1) area | N | 18% | 0
Energized work / hot work permits | N | 8% | 0
Hospital ICRA tier 3+ | N | 8% | 0
Heights > 14 ft (lift premium) | N | 5% | 0
Underground duct-bank concrete encasement | N | 6% | 0
Tight ceiling / plenum-rated cable upgrade | N | 4% | 0
After-hours / weekend / night shift | N | 20% | 0
Travel / per diem | N | 3% | 0
Cold-weather working conditions | N | 4% | 0
LEED documentation / Cx | N | 3% | 0
Owner-direct equipment (no markup) | N | -10% | 0
Premium $ total (applies-Y only)
Premium % total (applies-Y only)

## CSI Reference
CSI MASTERFORMAT — DIVISION 26 ELECTRICAL
26 00 00 | ELECTRICAL (overall division)
26 05 00 | Common Work Results for Electrical
26 05 19 | Low-Voltage Electrical Power Conductors and Cables
26 05 26 | Grounding and Bonding for Electrical Systems
26 05 29 | Hangers and Supports for Electrical Systems
26 05 33 | Raceways and Boxes for Electrical Systems
26 05 36 | Cable Trays for Electrical Systems
26 05 43 | Underground Ducts and Raceways for Electrical Systems
26 05 53 | Identification for Electrical Systems
26 08 00 | Commissioning of Electrical Systems
26 09 23 | Lighting Control Devices
26 09 26 | Lighting Control Panelboards
26 09 43 | Network Lighting Controls
26 22 00 | Low-Voltage Transformers
26 24 13 | Switchboards
26 24 16 | Panelboards
26 24 19 | Motor-Control Centers
26 25 00 | Enclosed Bus Assemblies
26 27 13 | Electricity Metering
26 27 16 | Electrical Cabinets and Enclosures
26 27 26 | Wiring Devices
26 27 73 | Door Chimes / Specialty Devices
26 28 13 | Fuses
26 28 16 | Enclosed Switches and Circuit Breakers
26 28 18 | Enclosed Circuit Breakers
26 29 13 | Enclosed Controllers
26 29 23 | Variable-Frequency Motor Controllers
26 32 13 | Engine Generators
26 36 23 | Automatic Transfer Switches
26 41 13 | Lightning Protection for Structures
26 43 13 | Surge Protective Devices
26 51 13 | Interior Lighting Fixtures, Lamps, and Ballasts
26 52 13 | Exterior Lighting Fixtures
26 53 00 | Exit Signs
26 56 00 | Sports / Stadium / Site Lighting
27 11 13 | Communications Copper Cable (cross-ref)
27 13 23 | Communications Optical Fiber (cross-ref)
28 13 00 | Access Control (cross-ref)
28 23 00 | Video Surveillance (cross-ref)
28 31 00 | Fire Detection and Alarm (cross-ref)