## Instructions
GROUND RESISTANCE TEST LOG — INSTRUCTIONS
PURPOSE
Captures every ground resistance measurement — 3-point fall-of-potential (acceptance),
clamp-on (verification), Wenner 4-point soil resistivity (design). Submission-ready for
AHJ + commissioning.
TYPICAL THRESHOLDS
• NEC 250.53(A)(2) — single rod electrode: ≤25 Ω or add second electrode.
• Hospital + data center spec: ≤5 Ω, sometimes ≤3 Ω.
• Telecom + sensitive electronics: ≤1 Ω.
TEST METHODS
3-point fall-of-potential: drive aux rods; measure resistance at 62% spacing.
Clamp-on: non-invasive; valid where multiple ground paths form a loop.
4-point Wenner: soil resistivity for design.
DOCUMENT VERSION
Ground_Resistance_Test_Log.xlsx v1.0 — 2026-05-19
ContrPro Complete Tier · Electrical Trade Pack

## Electrode Inventory
GROUNDING-ELECTRODE INVENTORY
# | Type (Rod/Ufer/Ring/Plate/Water) | Location | Size/Length | Install Date | Notes

## 3-Point Test Log
3-POINT FALL-OF-POTENTIAL TEST LOG
# | Date | Electrode Tested | Aux #1 Dist (ft) | Aux #2 Dist (ft) | Resistance (Ω) | Pass / Fail | Equipment Serial / Cal Date | Tester

## Clamp-On Test Log
CLAMP-ON TEST LOG
# | Date | Conductor / Path | Resistance (Ω) | Equipment Serial | Tester

## Soil Resistivity
SOIL RESISTIVITY (4-POINT WENNER)
# | Date | Site Location | Probe Spacing (ft) | Resistance (Ω) | Calc'd ρ (Ω·m) | Soil Type | Tester

## Reporting Summary
REPORTING SUMMARY
Category | Total Tests | Passed | Notes
3-Point Fall-of-Potential
Clamp-On Tests
Soil Resistivity Surveys
Electrodes Inventoried