## Instructions
PULL + INSULATION TEST LOG — INSTRUCTIONS
PURPOSE
Captures every feeder/branch pull + megger insulation test. AHJ + NETA-style acceptance
test format. Submission-ready for AHJ pre-energization inspection.
WORKFLOW
• Cable Pull Log — one row per pull. Captures circuit ID, raceway, conductor size,
pull tension (if engineered), pulling lube, length, completion date.
• Insulation Test Log — one row per megger test. Includes test voltage, duration,
result, NETA-style polarization index where required.
• Acceptance Sign-off — single record per feeder/system once all tests pass.
TYPICAL ACCEPTANCE THRESHOLDS
• 500 VDC test for ≤600V circuits — typical ≥100 MΩ.
• 1000 VDC test for medium-voltage — per spec.
• Polarization Index (PI) ≥ 2.0 for critical feeders (10 min ÷ 1 min reading).
• Disconnect equipment + neutrals before testing.
DOCUMENT VERSION
Pull_and_Insulation_Test_Log.xlsx v1.0 — 2026-05-19
ContrPro Complete Tier · Electrical Trade Pack

## Cable Pull Log
CABLE PULL LOG
# | Date | Circuit / Feeder ID | Raceway Type/Size | Conductor Size + Count | Length (ft) | Pull Tension (lbs) | Lube Used | Pulled By / Notes

## Insulation Test Log
INSULATION (MEGGER) TEST LOG
# | Date | Circuit / Feeder ID | Test Voltage (VDC) | Duration (s) | A-G (MΩ) | B-G (MΩ) | C-G (MΩ) | PI (10/1) | Pass/Fail | Tester | Notes

## Acceptance Sign-Off
ACCEPTANCE SIGN-OFF
# | Date | Feeder / System | Result (Pass/Fail) | Inspector Witness | Contractor Sign | Notes

## Reporting Summary
REPORTING SUMMARY
Category | Total | Passed | Notes
Cable pulls completed
Insulation tests completed
Insulation tests passed first-time
Insulation tests re-tested after repair
Feeders accepted