Raceway Selection by Environment

Conduit Fill (NEC Chapter 9 Table 1)

Conduit Support Spacing

Bend Radius + Pull Boxes

Conductor Selection (Ampacity + Voltage Drop)

Pull Tension Limits + Pulling Compound

Splices + Terminations

Voltage-Class Separation

Underground Raceway (NEC 300.5)

Acceptance Tests (Megger Insulation)

| Environment | Acceptable Raceway | Notes |
| --- | --- | --- |
| Interior, exposed, dry | EMT, RMC, IMC, MC cable, AC cable | EMT most common; verify hangers at proper spacing |
| Interior, concealed, dry (above-grade) | EMT, MC, AC, RMC, IMC | MC cable common in commercial drywall |
| Wet location indoor (cooler, wash-down) | RMC, IMC, PVC, liquidtight flex | Liquidtight for vibration loops |
| Outdoor, exposed | RMC, IMC, PVC schedule 80 (above grade) | PVC Schedule 80 only above-grade for above-ground use per NEC 352.10(F) |
| Underground direct burial | PVC schedule 40 / 80, RGS, IMC w/ approved coating | Concrete encasement may upgrade depth |
| Classified hazardous | RMC, IMC w/ explosion-proof fittings, MC-HL cable | NEC Article 500-516; engineering required |
| Plenum (above acoustic tile ceiling) | Plenum-rated cable (CMP, MPP), EMT | Verify ceiling category (return-air plenum vs. ducted) |
| Cable tray | Tray-rated cables (TC), single conductors in some applications | Article 392 fill limits |

NEC Chapter 9 Table 1 — maximum fill:

1 conductor: 53% of conduit cross-section.

2 conductors: 31%.

3 or more conductors: 40%.

Use Chapter 9 Tables 4 (raceway area) + 5 (conductor area) to verify. Or use a conduit
    fill calculator. ALSO verify NEC 310.15(B)(3)(a) ampacity adjustment for >3 CCC in raceway.

| Conduit | 40% fill area (sq in) | Approx. #12 THHN count |
| --- | --- | --- |
| 1/2" EMT | 0.122 | 9 |
| 3/4" EMT | 0.213 | 16 |
| 1" EMT | 0.346 | 26 |
| 1-1/4" EMT | 0.598 | 44 |
| 1-1/2" EMT | 0.814 | 60 |
| 2" EMT | 1.342 | 99 |
| 2-1/2" EMT | 2.343 | 173 |
| 3" EMT | 3.538 | 261 |
| 4" EMT | 6.140 | 454 |

| Type | Max Support Spacing (Horizontal) | Support Within |
| --- | --- | --- |
| EMT 1/2" - 3/4" | 10 ft | 3 ft of each box/fitting |
| EMT 1" - 2" | 10 ft | 3 ft of each box/fitting |
| EMT 2-1/2" - 4" | 10 ft | 3 ft of each box/fitting |
| RMC / IMC ≤1" | 10 ft | 3 ft of each box/fitting |
| PVC schedule 40 — 1/2" to 1" | 3 ft | 3 ft of each box/fitting |
| PVC schedule 40 — 1-1/4" to 2" | 5 ft | 3 ft of each box/fitting |
| PVC schedule 40 — 2-1/2" to 6" | 8 ft | 3 ft of each box/fitting |
| MC cable | 6 ft | 12 in of each box |
| AC cable | 4.5 ft | 12 in of each box |
| Flex (Greenfield) ≤ 1-1/4" | 4.5 ft (where required) | 12 in of each box |

Max 360° of bend between pull boxes (NEC 358.26 EMT, 344.26 RMC, 352.26 PVC).

Minimum bend radius — NEC Chapter 9 Table 2. PVC larger than steel.
            Example: 1" RGS / IMC = 5-3/4"; 1" PVC = 6"; 2" RGS = 9-1/2".

Pull boxes sized per NEC 314.28 — straight pulls ≥8× largest raceway;
            angle pulls per formula. Pull-box sizing failure is the most common rejection at
            rough-in inspection.

Ampacity — NEC Table 310.16. Calibrate for ambient temperature (310.15(B)(1))
            and number of CCCs in raceway (310.15(B)(3)(a)).

Voltage drop — informational, not mandatory by NEC, but typically targeted
            at ≤3% on branch + ≤5% combined (NEC Informational Note 215.2). Reference
            calculation = K × I × L / Cmils (single phase) or 1.732 × K × I × L / Cmils (3-phase),
            with K = 12.9 (copper) or 21.2 (aluminum) at 75°C.

Insulation rating — match the equipment terminal temperature limit
            (typically 60°C for breakers ≤100A; 75°C for >100A unless specifically marked otherwise).

Color code — NEC 200.6 (white = grounded), 250.119 (green = equipment
            ground), 210.5 + 215.12 (ungrounded conductors identified by system voltage).

Maximum pull tension limit — verify manufacturer spec; typical thumb rule = 0.008 × CM (copper
            single conductor). Exceeded tension damages insulation.

Pulling compound (lube) reduces friction by 30-60%. Match compound to insulation type
            (some lubes attack XLPE).

Sidewall pressure limit at bends — typical 500 lb/ft for solid dielectric.

Tugger + sheave size — verify cable manufacturer's minimum sheave diameter.

Document pull tension on the Pull Log if engineering required.

Splices in junction boxes only — NEC 300.15 except where specifically permitted.

UL-listed connectors (wire nuts to compression lugs). Sized to conductor + listed for
            material (copper-only, aluminum-only, or AL/CU).

Aluminum splices/terminations — anti-oxidant compound + listed AL/CU connector;
            NEC 110.14 listed.

Compression lugs — use the manufacturer's die + check with go/no-go gauge.

Strip length — match the connector spec. Too long = exposed conductor; too short = poor seat.

Torque to manufacturer spec — NEC 110.14(D) requires torque-wrench use where specified.

Class 1 and Class 2 wiring may NOT share a raceway except per NEC 725.136. Most installations
            keep them in separate conduits / cables.

Power (600V or less) vs. communications (Article 800) — minimum 2 in separation in open
            spaces; physical separation in shared trays.

Fire alarm (Article 760) — power-limited circuits separated from non-power-limited.

Verify by raceway labeling (NEC 110.21(B)) + tray section labels.

Burial depth per Table 300.5:

Direct burial 0-600V: 24" (residential branch 12-18" with GFCI / metallic conduit).

RGS / IMC: 6" cover.

PVC schedule 40 / 80 (non-concrete-encased): 18" cover.

PVC under building slab: 18" below slab.

Maintain 12" separation from other underground utilities or per local code.

Locator tape / tracer wire required for non-metallic raceway per many AHJs.

Sweeps + risers — long-radius bends; protect with bollards where exposed to vehicle traffic.

Concrete encasement per NEC 300.50 for medium voltage; reduces required cover.

Test feeders + branches with insulation resistance tester (megger). Typical commercial
            spec: 500 VDC for circuits ≤600V; 1000 VDC for medium voltage.

NETA acceptance criteria: minimum 100 MΩ at 500 VDC for solid dielectric cable in
            new installation; many specs require higher.

Apply test for 60 seconds; record reading at 60 s. Calculate Polarization Index (10 min ÷ 1
            min ratio) for critical feeders — >2 considered acceptable.

Disconnect equipment + neutrals before testing to prevent damage to electronics.

Document results on the Pull + Insulation Test Log XLSX. Submit to GC + AHJ if required.

Any reading below the specified threshold → investigate before energizing; do not
            "accept" with notation.