Grounding vs Bonding — Definitions

Grounding Electrode System (GES) — NEC 250.50-66

Equipment Grounding Conductor (EGC)

Bonding (Service + Building + Metal Piping)

Sizing Tables (Grounding Electrode + EGC)

Ground Resistance Testing (IEEE 81)

Connection Methods

Special Locations (Healthcare / Pool / Solar)

Common Errors

Test + Acceptance Procedures

Grounding — connection to earth via grounding electrode system (rods,
            plates, building steel, water pipe, etc.).

Bonding — connection of metallic components to provide a low-impedance
            fault-current path back to the source.

Grounding and bonding are TWO DIFFERENT FUNCTIONS that must both be performed properly.
            Grounding establishes earth reference; bonding ensures fault clearing.

NEC 250.50 requires ALL of the following present at the building to be bonded together
    into the GES:

Metal underground water pipe in direct contact with earth ≥10 ft (250.52(A)(1)).

Metal in-ground support structure (concrete-encased rebar / Ufer) — 250.52(A)(3).

Concrete-encased electrode (Ufer) — minimum 20 ft of #4 AWG bare copper
            OR 1/2" rebar in foundation footing, in direct contact with earth.

Ground ring — at least 20 ft of #2 AWG bare copper buried at least 30" deep.

Rod / pipe electrode — 5/8" × 8 ft min, driven full length, 6" max above ground.

Plate electrode — at least 2 sq ft surface area.

Other listed local metal underground systems.

NEC 250.118 lists acceptable EGCs:

Copper / aluminum conductor in conduit.

RMC, IMC, EMT (where listed as EGC).

MC cable (with metal sheath listed as EGC) or AC cable.

Type AC armored cable (with proper bonding strip).

Flex / liquid-tight only with length limits + separate EGC if longer than spec.

NEC 250.122 sizes the EGC based on circuit ampacity. Larger feeder → larger EGC.

Service bonding — main bonding jumper connects grounded conductor (neutral)
            to grounding electrode + equipment grounding bus AT THE SERVICE only. NEC 250.24.

Separately derived systems — generators, transformers — system bonding
            jumper at the source side. NEC 250.30.

Metal water piping — bonded per NEC 250.104(A): water pipe within 5 ft
            of entry must be bonded; sizing per 250.66.

Metal gas piping — bonded per NEC 250.104(B). CSST manufacturer may require
            additional bonding for lightning protection — verify per CSST listing.

Metal building structure — bonded per NEC 250.104(C) for buildings supplied
            by feeder or branch circuit.

Pools + spas — equipotential bonding per Article 680.

| Largest ungrounded service-entrance conductor / equivalent for parallel sets | Copper GEC | Aluminum GEC |
| --- | --- | --- |
| 2 AWG or smaller | 8 AWG | 6 AWG |
| 1 AWG or 1/0 | 6 AWG | 4 AWG |
| 2/0 or 3/0 | 4 AWG | 2 AWG |
| Over 3/0 through 350 kcmil | 2 AWG | 1/0 AWG |
| Over 350 through 600 kcmil | 1/0 AWG | 3/0 AWG |
| Over 600 through 1100 kcmil | 2/0 AWG | 4/0 AWG |
| Over 1100 kcmil | 3/0 AWG | 250 kcmil |

| Rating of OCPD (A) | Copper EGC | Aluminum EGC |
| --- | --- | --- |
| 15 A | 14 AWG | 12 AWG |
| 20 A | 12 AWG | 10 AWG |
| 60 A | 10 AWG | 8 AWG |
| 100 A | 8 AWG | 6 AWG |
| 200 A | 6 AWG | 4 AWG |
| 400 A | 3 AWG | 1 AWG |
| 600 A | 1 AWG | 2/0 AWG |
| 1200 A | 3/0 AWG | 250 kcmil |

3-point fall-of-potential — gold standard for new installations.
            Drive auxiliary electrodes; measure resistance at 62% spacing.

Clamp-on — non-invasive but only valid where multiple ground paths form
            a loop. Useful for follow-up but not the initial acceptance.

Soil resistivity — Wenner 4-point method when designing the GES for
            critical loads (data centers, hospitals).

NEC 250.53(A)(2) single-rod threshold: ≤25Ω OR drive a second electrode.

Critical installations may spec ≤5Ω or ≤3Ω — verify spec.

Document on Ground Resistance Test Log XLSX.

Acorn clamp — for ground rod to bare copper. Listed for direct burial
            (250.70). One ground rod connection per clamp typically.

Compression connector — for cable-to-rebar / cable-to-cable.
            Listed for application.

Exothermic weld (Cad-weld) — permanent connection. Required by many
            specs for grounding electrode connections in critical installations.

Bus connections — proper torque to mfr specs. Anti-oxidant compound on
            aluminum connections.

All connections accessible per 250.68 except direct-buried, encased, or otherwise
            permitted.

Healthcare (Article 517) — patient-care areas have additional bonding requirements.
            Operating rooms + critical-care areas require redundant equipment grounding.

Pools + Spas (Article 680) — equipotential bonding grid bonds all metallic
            components within 5 ft horizontally + 12 ft vertically of pool perimeter.

Solar PV (Article 690) — DC + AC equipment grounding; metal frames bonded;
            specific listed grounding hardware.

Generators (Article 445) — bonding of generator frame; system bonding jumper
            location depends on whether separately derived.

Hazardous locations (Articles 500-516) — explosion-proof bonding fittings;
            no flex bonded through bushings only.

Single ground rod with no resistance test (NEC 250.53 violation).

Main bonding jumper omitted at service.

Separately-derived system bonded at downstream panel instead of at the source.

Water pipe bonding tap > 5 ft from entry.

EGC undersized for branch / feeder OCPD (Table 250.122 missed).

Aluminum EGC at termination without anti-oxidant + torque verification.

Flex used as EGC beyond length / size allowance (250.118).

Metal water pipe used as sole grounding electrode (NEC 250.52 requires additional electrode).

Concrete-encased electrode (Ufer) omitted on new construction with rebar foundation.

Ground bus connections not torqued per spec.

Visual inspection — every connection accessible, properly torqued, oxidation-free,
            UL-listed components.

Continuity test — every EGC + GEC to its termination.

3-point fall-of-potential ground resistance test — record values; submit to AHJ.

Compare against spec / NEC 250.53.

Document on Ground Resistance Test Log XLSX with date, tester, equipment serial,
            and result.

Photograph each grounding electrode + connection before backfill / encasement.