Hierarchy of Controls — De-Energize First

LOTO Step-by-Step

Voltage Verification (Test-the-Tester)

Energized Work Permit (EWP)

Arc-Flash Boundary + PPE Categories

Shock Protection Boundaries

Arc-Rated PPE Selection Matrix

Qualified vs Unqualified Persons

NEC 110.16 Field Labeling

Incident Response

OSHA + NFPA 70E require: de-energize first. Energized work is the last resort, allowed
    only when:

De-energization creates a greater hazard (life-safety circuits, ventilation).

De-energization is infeasible (troubleshooting, voltage measurement).

Operation involves voltages < 50 V with no exposure to arc-flash hazard.

If any of the above apply, an Energized Work Permit (EWP) must be issued + signed.

Identify energy sources. All of them — utility, generator, UPS, battery, control,
            stored mechanical / hydraulic / pneumatic.

Notify affected persons. Coordinate with building operations on live-building projects.

Open the disconnect / breaker. Verify position visually + by labeling.

Apply lock + tag. Each worker applies their OWN lock. Multiple workers → multi-lock hasp.

Test for absence of voltage. Use a known-good meter. TEST THE TESTER on a live source
            BEFORE the verification AND AFTER. Confirms your meter is working.

Discharge stored energy. Capacitors, springs, hydraulic accumulators.

Perform work.

On completion: remove tools, notify affected persons, remove personal lock + tag, restore energy.

Use a meter rated for the voltage class being tested (CAT II / III / IV).

Test the meter on a known-live source BEFORE the verification.

Verify zero voltage on the de-energized circuit — phase-to-phase, phase-to-ground.

Test the meter again on the known-live source AFTER the verification. Confirms the meter
            didn't fail to a "zero" reading during the test.

Document on the LOTO log + EWP.

Required for any energized work over 50 V. Per NFPA 70E 110.4. The permit documents the
    risk assessment, controls, and signatures.

| Work description | What is being done + why de-energization is infeasible |
| --- | --- |
| Equipment + voltage | Equipment ID + nominal voltage + available fault current |
| Shock boundary | Limited / Restricted approach boundary distances |
| Arc-flash boundary | From engineered study or 70E Table 130.5(C) |
| Incident energy | cal/cm² at working distance |
| Required PPE | PPE Category + specific items verified on site |
| Qualified worker(s) | Name + qualification per 1910.332 + 70E 110.6 |
| Job briefing | Performed + documented |
| Tool verification | Insulated tools + meters within cert |
| Signatures | Qualified employee + supervisor + safety officer |

Log every issued EWP on the companion XLSX.

Project-specific engineered arc-flash study (if available) controls. Without a study,
    NFPA 70E Table 130.7(C)(15)(a)/(b) defaults apply by equipment class.

| PPE Cat | Min Incident Energy (cal/cm²) | Arc-Rated Clothing | Other PPE |
| --- | --- | --- | --- |
| 1 | 4 | AR shirt + pants OR coverall (4 cal/cm²) | Hard hat, AR face shield, safety glasses, AR gloves + leather, ear inserts |
| 2 | 8 | AR shirt + pants OR coverall (8 cal/cm²) | + AR balaclava |
| 3 | 25 | AR shirt + pants + coverall OR AR flash suit jacket + pants (25) | + AR hood with arc-rated viewing window |
| 4 | 40 | AR flash suit jacket + pants OR coverall (40) | + AR hood |

| Voltage (V phase-to-ground) | Limited Approach (Exposed Movable Cond) | Restricted Approach |
| --- | --- | --- |
| 50 - 300 | 10 ft 0 in (avoid contact) | Avoid contact |
| 301 - 750 | 3 ft 6 in | 1 ft 0 in |
| 751 V - 15 kV | 5 ft 0 in | 2 ft 2 in |
| 15 kV - 36 kV | 6 ft 0 in | 2 ft 7 in |

Exact values from NFPA 70E Table 130.4(E)(a) — fixed-circuit / exposed-movable distances.
    Round up + verify against current edition.

Each worker performing work within the arc-flash boundary must be equipped with arc-rated
    PPE at or above the incident energy. Layering: arc-rated outer layer +
    natural-fiber inner layer (no synthetic). PPE is verified daily before each EWP.

Arc-rated head protection — hard hat with AR face shield or hood.

Hearing protection — ear-canal inserts (foam plugs).

Arc-rated eyewear — safety glasses (worn UNDER face shield).

Arc-rated hand protection — rubber insulating gloves with leather protectors;
            test gloves per ASTM F496 every 6 months.

Arc-rated foot protection — dielectric or EH-rated leather boots.

Non-conductive tools — insulated to test voltage rating; visually inspect for cuts.

OSHA 1910.332 + NFPA 70E 110.6 require workers exposed to electrical hazards be
    "qualified" — trained in:

Skills + techniques to distinguish exposed live parts from other parts.

Skills + techniques to determine nominal voltage.

Clearance distances + voltages.

Selection + use of test instruments.

Practices of safe work near energized equipment.

How to apply LOTO.

Recognition + avoidance of electrical hazards.

Training documented + refreshed per the employer's program (typically annually). An
    unqualified person may not enter the limited-approach boundary of an exposed energized
    conductor without escort + direct supervision by a qualified person.

Switchboards, panelboards, industrial control panels, meter socket enclosures, and
            motor control centers in non-dwelling occupancies require a permanent warning label.

Label content: warning of arc-flash + shock hazard, equipment ID, date applied.

NEC 110.16(B) — service equipment ≥1200 A in non-dwelling: label must also include
            nominal voltage, available fault current, clearing time of OCPD, date.

Engineered arc-flash study labels add: incident energy at working distance, arc-flash
            boundary distance, required PPE category.

Verify labels before energizing; replace any damaged labels promptly.

Electrical contact victim — never touch a victim still in contact with energy.
            Cut power first or use insulated rescue equipment.

Arc-flash victim — burns are the immediate hazard. Cool with water
            (clean), cover with sterile dressing if available, transport to ER. Eye exposure to
            arc light → ophthalmology evaluation even if no immediate symptom.

Trapped worker in energized enclosure — emergency call, follow site
            EAP. Coordinate with controlling contractor on rescue without secondary contact.

Investigation — document the incident under OSHA 1904.39 if hospitalization
            within 24 hours. Preserve scene + meters / tools / PPE.