This Site-Specific Electrical Safety Plan ("SSEP") is the electrical contractor's
        project-specific roadmap covering NEC compliance, NFPA 70E electrical safety, lockout/
        tagout, arc-flash boundaries, energized work, AHJ inspection sequencing, and multi-trade
        coordination. Tailor every variable to the actual project, walk it with the GC and the
        AHJ electrical inspector at the pre-construction meeting, and sign at Section 16.
        OSHA Multi-Employer Citation Policy applies — controlling contractor + electrical
        contractor are jointly citable for site-specific violations.

Parties & Project Identification

Permits, AHJ & NEC Edition

Inspection Sequence (UG / Rough / Service / Final)

Electrical Scope of Work

Lockout / Tagout Program (1910.147)

NFPA 70E Electrical Safety — Energized Work + Arc-Flash

Temporary Power & GFCI

Working at Heights — Lifts, Ladders, Tools

Trenching & Underground Raceway (Subpart P)

Hazmat Encountered (Asbestos / Lead / PCBs)

Multi-Trade Coordination

Occupied-Building / Live-Building Considerations

Acceptance Testing & Commissioning

Emergency Response

Stop-Work Triggers

Signatures

| Project Name | [Project Name] |
| --- | --- |
| Project Address | [Address] |
| Owner | [Owner + Rep] |
| General Contractor (controlling) | [GC + Project Manager] |
| Electrical Engineer of Record | [MEP Firm + EOR stamp] |
| Electrical Contractor | [Contractor Legal Name] |
| Electrical State License # | [License # + Master Electrician of Record] |
| Electrical Superintendent | [Name + Phone] |
| Foreman | [Name + Phone] |
| Service Size | [Amps / Volts / Phase] |
| Estimated Start | [Date] |
| Substantial Completion | [Date] |
| Project Type | [New / Renovation / Tenant Fit-out / Adaptive Reuse] |
| Building Occupancy / Construction Type | [IBC Ch 3 / Ch 6] |

| Electrical Permit # | [Permit + issue date] |
| --- | --- |
| AHJ — Electrical Inspector | [Name + Cell + Email] |
| Inspection Request Method | [Portal / Phone + Lead Time] |
| Adopted NEC Edition | [NEC 2023 + Local Amendments] |
| Utility Coordinator (Power Company) | [Utility + Acct + Coordinator] |
| Pre-Energization Test Lab | [NETA cert vendor if applicable] |
| Adopted NFPA 70E Edition | [NFPA 70E 2024 + Local Adoption] |

| Inspection | Trigger | What Gets Inspected |
| --- | --- | --- |
| Underground Raceway | Before backfill / encasement | Conduit routing, depth (NEC 300.5), bedding, mandrel pull-test if specified, separation from other utilities |
| Rough-In | Before drywall | Boxes set, conduit + wire installed (some AHJs require unfinished conductors), grounding electrode system, bonding, mounting heights |
| Service / Meter | Before energization | Service-entrance conductors, meter base, main disconnect, grounding electrode system, bonding, working clearance (NEC 110.26) |
| Pre-Energization Acceptance | Pre-utility-tie | Megger test feeders, ground resistance test, panel exercise, arc-flash labels per NEC 110.16, NETA test report if specified |
| Trim Out / Devices | Before final | Devices set + tested, GFCI/AFCI verification, polarity, working illumination |
| Final | Pre-TCO | All circuits labeled, panel schedules complete, working illumination, exit signs functional, emergency battery test 90-min, fire-alarm cert on file |

| CSI Code | System | Scope |
| --- | --- | --- |
| 26 05 | Common Work Results — raceway, wire, supports, grounding | BY US |
| 26 24 13 | Switchboards (service entrance) | [scope — BY US / by switchgear vendor] |
| 26 24 16 | Panelboards | BY US |
| 26 27 13 | Service Entrance + Meter | BY US to utility meter; utility side BY OTHERS |
| 26 32 13 | Engine Generators | [BY US / BY OTHERS — vendor commissioning included?] |
| 26 36 23 | Automatic Transfer Switches | [scope] |
| 26 41 13 | Lightning Protection | [BY US / specialty sub] |
| 26 51 13 | Interior Lighting | BY US — fixtures owner-direct or contractor-supplied? |
| 26 52 13 | Exterior Lighting + Site | [scope] |
| 27 11 | Communications cabling | [scope — by EC or by IT vendor] |
| 28 31 | Fire Detection + Alarm | [BY US — design-build / by fire-alarm sub] |
| 28 13/23 | Access Control / Video | [BY US / by specialty sub] |
| 33 71 | Underground Utility Power | [BY US / by utility / shared with site] |

Every job must have a written LOTO program. Every energized circuit a worker touches must
    be verified de-energized + locked + tagged. Recurring training documented.

Identify all energy sources for the equipment / circuit (utility, generator, UPS, battery, control).

Notify affected persons; coordinate with operations on live-building projects.

Open the disconnect / breaker. Verify the disconnect is in OFF position.

Apply individual lock + tag. Each worker on the job applies HIS OR HER OWN lock.

Test for voltage with a known-good meter. Test the meter on a live source before AND after the verification — confirms the meter itself is working.

Discharge stored energy (capacitors, springs, hydraulic).

Perform work.

On completion: remove personal tools, notify affected persons, remove personal lock + tag, restore energy.

De-energize first. Only justify energized work per NFPA 70E 110.4 — additional hazards
    of de-energization, infeasibility of de-energizing (life-safety circuits, troubleshooting),
    or operations <50 V where no arc-flash hazard exists.

Required for any energized work over 50 V. Permit must document:

Work to be performed + justification why de-energization is infeasible.

Shock-protection boundary + arc-flash boundary based on engineered study OR NFPA 70E Table 130.5(C).

PPE required + verified on site (arc-rated clothing, gloves with leather protectors, face shield, etc.).

Job briefing performed; tools verified; safe work practices reviewed.

Worker qualified per 1910.332 + 70E 110.6.

Authorized signatures: qualified employee + supervisor + safety officer.

Project-specific arc-flash study (engineered) controls when available. Without a study,
    NFPA 70E Table 130.7(C)(15) defaults apply.

| PPE Cat | Incident Energy (cal/cm²) | Arc-Rated Clothing | Equipment |
| --- | --- | --- | --- |
| 1 | 4 | AR shirt + pants OR coverall (rated 4) | Hard hat + AR face shield + safety glasses + AR gloves + leather + ear canal inserts |
| 2 | 8 | AR shirt + pants OR coverall (rated 8) | Hard hat + AR balaclava + AR face shield + safety glasses + AR gloves + leather + ear inserts |
| 3 | 25 | AR shirt + pants + coverall OR AR flash suit jacket + pants (rated 25) | Hard hat + AR hood + safety glasses + AR gloves + leather + ear inserts |
| 4 | 40 | AR flash suit jacket + pants OR flash suit coverall (rated 40) | Hard hat + AR hood + safety glasses + AR gloves + leather + ear inserts |

Switchboards, panelboards, industrial control panels, meter socket enclosures, and
            motor control centers in non-dwelling occupancies require warning labels.

NEC 110.16(B) requires service equipment ≥1200 A in non-dwelling occupancies to also
            list nominal voltage, available fault current, clearing time of OCPD, date of label.

Engineered arc-flash study labels add incident energy + arc-flash boundary + working
            distance + PPE category.

All 15A and 20A 125V receptacles used by construction personnel must be GFCI protected
            (1926.404(b)(1)(ii)).

Alternative: documented Assured Equipment Grounding Conductor Program.

Temporary power panels — proper service rating, grounding electrode system, weather-
            tight if outdoors, lockable disconnect.

Cords — extra-hard usage (S, SE, SO, ST, STO, SOO), no splices except molded plug-end
            replacement, no Romex through doorways or as building wiring.

Daily inspection of cords + GFCI test pre-shift.

Fall protection at heights > 6 ft (construction) per OSHA 1926.501.

Aerial lift / scissor lift training current; daily inspection of fall-arrest anchor.

Ladder selection: extension ladder reaches 3 ft above landing; A-frame fully open + locked.

Working on energized circuits at heights → consider arc-flash PPE + 4-point harness +
            tool tethering.

Hot work in lifts — fire watch from ground if welding/grinding sparks could fall on
            combustibles.

Call 811 minimum 2 business days before digging.

Designate Competent Person per 1926.651(k) trained in soil classification + protective systems.

Soil classification: Type A/B/C per 1926 App A.

Trench >4 ft requires ladder/step within 25 ft.

Trench >5 ft requires protective system (slope/shore/shield) unless solid rock.

Spoil pile ≥2 ft from edge.

NEC depth: 600V or less direct burial — 24" cover (NEC Table 300.5); other depths
            for conduit + duct-bank concrete encasement.

Maintain 12" separation from other utilities or per local code.

Asbestos — pre-1980 buildings may have ACM in conduit fittings, fire-stop,
            cement-board. Survey before disturbance.

Lead-based coatings — pre-1978 buildings may have lead paint on conduit,
            boxes, or wall surfaces. RRP-certified renovator required.

PCBs — old fluorescent ballasts (pre-1979) + transformers may contain PCBs.
            Disposal per 40 CFR 761. Coordinate hazwaste vendor; document chain-of-custody.

Mercury — old fluorescent tubes contain mercury. Break-and-bag is OSHA
            violation; use crushers with vapor control or universal-waste recycler.

Coordination drawings overlay EC against M / FP / Plumb / S — clashes resolved
            before installation.

Above-ceiling priority sequence — confirm at GC coordination meeting.

Sleeves + slab penetrations coordinated with concrete.

Lighting layout vs. ductwork / sprinkler heads — confirmed via reflected ceiling plan
            overlay.

Power for plumbing/mechanical equipment — confirm final-connection scope split.

Live-cutover plan — define every step from de-energization through re-energization,
            including circuit-by-circuit timing. Coordinate with owner ops + life-safety vendor.

Occupant notification — 48-hour minimum for planned outages; off-hours work where feasible.

Tie-in to existing — verify panel directory current; door labels match installed circuits.

ICRA (hospitals) — coordinate with infection-control preventionist; HEPA + containment
            per ICRA tier.

UPS / emergency-system handover — never interrupt without owner's written authorization.

Megger insulation test — feeders + branch conductors ≥600V; record results;
            replace any conductor below the standard threshold.

Ground resistance test — 3-point fall-of-potential per IEEE 81. Target
            ≤25 Ω (NEC 250.53 single-rod) or ≤5 Ω where required by spec.

Panel + breaker exercise — open + close every breaker; verify trip on a known
            overload (where lab-test possible) or per NETA acceptance criteria.

Bonding continuity — verify with ohmmeter or ground tester.

Arc-flash labeling — install labels per NEC 110.16 + engineered study (if any).

Fire-alarm certification — by fire-alarm sub; integration with EC scope verified.

Emergency-system 90-minute battery test — per NEC 700.3(C) and NFPA 110.

Lighting controls + occupancy sensor — verify per spec sequence of operation.

| Site First-Aid Station / AED | [Location] |
| --- | --- |
| Nearest Hospital + ER | [Name + address + drive time] |
| Site Emergency Contact | [GC superintendent + cell] |
| Utility Emergency (24-hr) | [Power company emergency line] |
| Main Service Disconnect | [Location + responsible person] |
| Hazmat / PCB Vendor | [24-hr phone] |
| 911 Address Reciprocity | [How EMS finds site — gate code, exact entry] |

Energized circuit encountered without LOTO or EWP.

Arc-flash incident energy > 40 cal/cm² without engineered controls.

Suspected ACM, lead-based paint, or PCBs disturbed.

Trench cave-in risk or unsafe access.

NEC working clearance (110.26) violated — equipment placement requires field reroute.

Code-edition conflict between drawings and AHJ adopted code.

GFCI tripping on temp power and not resetting (ground fault present).

Insulation test failure on a circuit that hasn't been remediated.

Worker injury exceeding first-aid level.

The undersigned have reviewed this SSEP and concur with the procedures, responsibilities,
    and stop-work triggers.

Revision history: log each substantive change with date, page, signer. Post current
        version at trailer; archive older.