## Instructions
MECHANICAL BID ESTIMATOR — INSTRUCTIONS
PURPOSE
Production estimating tool for commercial mechanical (HVAC + hydronic + refrigeration)
contractors. Combines per-equipment + per-ton + per-CFM + per-LF of pipe / per-SF of
sheet-metal anchors. CSI Division 23 primary with cross-references to 22 (plumbing),
26 (electrical), and 27 (BAS / controls).
WORKFLOW
1. Project Info — fill every blue field.
2. Wage Rates — set base + fringe + burden by classification.
3. Material Takeoff — quantities by CSI line item.
4. Labor Estimate — productivity defaults assume average commercial conditions.
5. Equipment — daily/weekly rentals + tools.
6. Subcontract — TAB, refrigerant charging, controls programming, etc.
7. Premiums — height, healthcare, occupied building, prevailing wage.
8. Bid Summary — automatic roll-up + final bid.
LABOR UNITS
Anchors used: per-ton or per-CFM for equipment-set, per-LF by diameter for piping,
per-SF for sheet-metal (gauge-adjusted), per-each for terminals + accessories.
Calibrate against your historical job-cost. Underestimating labor is the most common
cause of mechanical-bid losses.
FIELD-ONLY SCOPE
Calibrated for field installation. Sheet-metal fab-shop production work is typically
in-house or subbed and not estimated here — material costs reflect delivered fabricated
ductwork. Pre-fabricated piping rack assemblies similarly.
DOCUMENT VERSION
Mechanical_Bid_Estimator.xlsx v1.0 — 2026-05-19
ContrPro Complete Tier · Mechanical Trade Pack

## Bid Summary
BID SUMMARY — Mechanical Trade Pack
Material total (incl. tax)
Labor total
Equipment total
Subcontract total
Premiums $
Direct cost subtotal
Premium % applied
Premium % adder $
Direct + premium %
| Contingency % | 5%
Contingency $
Direct + contingency
| Overhead % | 10%
Overhead $
| Profit % | 10%
Profit $
| Bond % | 1.2%
Bond $
| Insurance / GL % | 1.8%
Insurance $
FINAL BID

## Project Info
PROJECT INFORMATION
Project Name
Project Address
Owner
General Contractor
Architect / Engineer
Bid Due Date
Bid Reference / Number
Project Type | (New / Renovation / Tenant fit-out / Adaptive reuse)
Building Use | (Office / Retail / Healthcare / Education / Multi-family / Hospitality / Industrial)
Approx. Square Footage
Stories
Total Tonnage (cooling)
Total CFM (supply / return / OA)
AHJ — Mechanical Inspector
Applicable Mechanical Code | (IMC 2024 / UMC 2024 / local amendments)
Applicable Energy Code | (IECC 2021 / ASHRAE 90.1-2019 / state amendments)
Estimator Name
Date Prepared
Internal Bid Number
Notes / Assumptions

## Wage Rates
WAGE RATES (calibrate to your market)
Classification | Base Rate ($/hr) | Fringe ($/hr) | Burden % (WC/GL/FICA) | OT Premium (1.5×) | Loaded Rate ($/hr)
Mechanical Foreman | 62 | 19.5 | 32%
Sheet Metal Journeyman | 50 | 18.5 | 32%
Pipefitter Journeyman | 54 | 19.5 | 32%
Steamfitter Journeyman | 56 | 19.5 | 32%
Refrigeration Tech (EPA 608) | 58 | 19.5 | 32%
HVAC Tech | 50 | 18.5 | 32%
Apprentice (Yr 4) | 38 | 14 | 32%
Apprentice (Yr 2) | 28 | 12 | 32%
Insulator | 42 | 16 | 32%
Helper / Material Handler | 22 | 9.5 | 32%
Controls Tech / BAS | 60 | 19 | 32%
TAB Technician | 55 | 18 | 32%

## Material Takeoff
MATERIAL TAKEOFF (CSI Division 23)
CSI Code | Description | QTY | UOM | Unit Cost ($) | Material Subtotal ($) | Notes
23 05 13 | Pipe hangers + supports — clevis 1" - 4" | 0 | EA | 9.5
23 05 13 | Trapeze + unistrut assembly (multi-pipe) | 0 | EA | 38
23 05 17 | Sleeves + escutcheons (per assembly) | 0 | EA | 6.5
23 05 23 | Valve — ball, bronze, 1" | 0 | EA | 28
23 05 23 | Valve — ball, bronze, 2" | 0 | EA | 65
23 05 23 | Valve — globe, bronze, 1" | 0 | EA | 65
23 05 23 | Valve — butterfly, cast iron, 4" | 0 | EA | 185
23 05 23 | Valve — gate, cast iron, 6" | 0 | EA | 425
23 07 13 | Duct insulation — fiberglass wrap, 1.5" w/ FRK | 0 | SF | 1.85
23 07 13 | Duct insulation — fiberglass duct liner, 1" | 0 | SF | 2.65
23 07 19 | Pipe insulation — fiberglass, 1" pipe | 0 | LF | 2.85
23 07 19 | Pipe insulation — fiberglass, 2" pipe | 0 | LF | 4.2
23 07 19 | Pipe insulation — fiberglass, 4" pipe | 0 | LF | 7.85
23 07 19 | Pipe insulation — Armaflex, 1" pipe | 0 | LF | 3.85
23 09 13 | BAS controller — VAV box | 0 | EA | 485
23 09 13 | BAS controller — AHU controller | 0 | EA | 1450
23 09 23 | Direct Digital Control (DDC) panel — 32-pt | 0 | EA | 3850
23 09 33 | Thermostat — programmable | 0 | EA | 145
23 09 33 | Thermostat — networked, BAS | 0 | EA | 385
23 09 33 | Sensor — temperature, duct-mount | 0 | EA | 65
23 09 33 | Sensor — pressure, differential | 0 | EA | 185
23 09 33 | Sensor — CO2 / IAQ | 0 | EA | 285
23 11 13 | Fuel oil tank — 275 gal indoor | 0 | EA | 1850
23 11 23 | Natural gas piping — black iron 1" | 0 | LF | 8.5
23 11 23 | Natural gas piping — black iron 2" | 0 | LF | 16.5
23 21 13 | Hydronic — copper Type L, 3/4" | 0 | LF | 6.85
23 21 13 | Hydronic — copper Type L, 1" | 0 | LF | 9.4
23 21 13 | Hydronic — copper Type L, 2" | 0 | LF | 18.5
23 21 13 | Hydronic — black steel, 2" | 0 | LF | 8.5
23 21 13 | Hydronic — black steel, 4" | 0 | LF | 18.85
23 21 13 | Hydronic — PEX-A w/ oxygen barrier, 1" | 0 | LF | 1.85
23 21 16 | Hydronic — pre-insulated underground | 0 | LF | 38
23 21 23 | Circulator pump — 1/12 HP inline | 0 | EA | 285
23 21 23 | Circulator pump — 1 HP base-mounted | 0 | EA | 1450
23 21 23 | End-suction pump — 5 HP | 0 | EA | 3850
23 21 29 | Expansion tank — 30 gal | 0 | EA | 485
23 21 29 | Air separator — 4" | 0 | EA | 685
23 22 13 | Steam piping — black steel, 2" | 0 | LF | 10.85
23 22 16 | Steam trap — F&T 3/4" | 0 | EA | 285
23 25 13 | Glycol fill (per gallon) | 0 | GAL | 18.5
23 25 13 | Chemical pot feeder | 0 | EA | 485
23 31 13 | Galvanized rectangular duct — 24ga | 0 | SF | 8.5
23 31 13 | Galvanized rectangular duct — 22ga | 0 | SF | 9.85
23 31 13 | Galvanized rectangular duct — 20ga | 0 | SF | 11.5
23 31 13 | Galvanized round duct — spiral, 24ga | 0 | SF | 7.5
23 31 13 | Galvanized round duct — spiral, 22ga | 0 | SF | 8.85
23 31 16 | Stainless steel duct — 22ga (kitchen exhaust) | 0 | SF | 28.5
23 31 19 | Flex duct — insulated, 6" | 0 | LF | 4.85
23 31 19 | Flex duct — insulated, 12" | 0 | LF | 9.85
23 33 13 | Volume damper — manual, 12" | 0 | EA | 85
23 33 13 | Motorized damper — 24V actuator, 12" | 0 | EA | 385
23 33 33 | Fire damper — 1.5-hr UL listed, 12" | 0 | EA | 285
23 33 33 | Smoke damper — UL 555S, 12" | 0 | EA | 485
23 33 33 | Combination fire / smoke damper, 12" | 0 | EA | 685
23 33 46 | Flexible duct connector | 0 | LF | 14.5
23 34 13 | Exhaust fan — inline 250 CFM | 0 | EA | 485
23 34 13 | Exhaust fan — roof-mount 500 CFM | 0 | EA | 1485
23 34 13 | Exhaust fan — kitchen hood 4000 CFM UL 762 | 0 | EA | 4850
23 34 16 | Supply fan — inline 800 CFM | 0 | EA | 685
23 36 16 | VAV box — fan-powered 600 CFM | 0 | EA | 1685
23 36 16 | VAV box — single-duct 800 CFM | 0 | EA | 1185
23 36 16 | VAV box — single-duct 1200 CFM | 0 | EA | 1485
23 37 13 | Supply diffuser — 4-way, 24x24 | 0 | EA | 38.5
23 37 13 | Return grille — 24x24 | 0 | EA | 22.5
23 37 13 | Exhaust grille — 12x12 | 0 | EA | 14.5
23 37 13 | Linear slot diffuser — 6 ft | 0 | EA | 285
23 41 13 | MERV 8 filter — 20x25x2 | 0 | EA | 9.5
23 41 13 | MERV 13 filter — 20x25x4 | 0 | EA | 38.5
23 41 13 | HEPA filter — 24x24x12 (hospital) | 0 | EA | 285
23 51 13 | B-vent — single wall 6" | 0 | LF | 18.5
23 51 13 | Stainless flue — 6" | 0 | LF | 65
23 52 13 | Gas-fired boiler — 500 MBH atmospheric | 0 | EA | 5850
23 52 16 | Gas-fired boiler — 1500 MBH condensing | 0 | EA | 18500
23 52 39 | Electric boiler — 30 kW | 0 | EA | 6500
23 54 13 | Furnace — gas, 80% AFUE 80 MBH | 0 | EA | 1850
23 54 16 | Furnace — gas, 96% AFUE 80 MBH | 0 | EA | 2850
23 57 13 | Plate-and-frame HX, 100 GPM | 0 | EA | 4850
23 62 13 | DX split — 3 ton outdoor unit | 0 | EA | 2850
23 62 13 | DX split — 5 ton outdoor unit | 0 | EA | 4250
23 62 13 | VRF outdoor — 10 ton | 0 | EA | 18500
23 62 13 | Mini-split outdoor — 18 MBH | 0 | EA | 1685
23 62 23 | Refrigerant piping — Type ACR copper 5/8" | 0 | LF | 4.85
23 62 23 | Refrigerant piping — Type ACR copper 7/8" | 0 | LF | 7.85
23 64 16 | Air-cooled chiller — 60 ton scroll | 0 | EA | 38500
23 64 19 | Water-cooled chiller — 200 ton centrifugal | 0 | EA | 125000
23 65 13 | Cooling tower — 200 ton crossflow | 0 | EA | 38500
23 72 13 | ERV — 1000 CFM packaged | 0 | EA | 6850
23 73 13 | Indoor AHU — 3000 CFM packaged | 0 | EA | 9500
23 73 13 | Indoor AHU — 8000 CFM custom-built-up | 0 | EA | 24500
23 73 23 | Rooftop unit — 5 ton packaged | 0 | EA | 5850
23 73 23 | Rooftop unit — 15 ton packaged | 0 | EA | 18500
23 73 23 | Rooftop unit — 25 ton packaged | 0 | EA | 32500
23 81 13 | Fan coil unit — vertical, 800 CFM | 0 | EA | 1485
23 81 23 | Ductless mini-split — 18 MBH indoor head | 0 | EA | 485
23 81 26 | Heat pump — 4 ton split outdoor unit | 0 | EA | 4850
23 83 13 | Radiant floor tubing — 1/2" PEX | 0 | LF | 1.05
23 83 13 | Radiant manifold — 6 loop | 0 | EA | 685
23 00 10 | Permit — mechanical | 0 | LS | 0 |  | Allowance
Material Subtotal
|  |  |  | Sales tax % | 7%
Sales tax $
Material TOTAL (incl tax)

## Labor Estimate
LABOR ESTIMATE (MCAA/SMACNA-style)
CSI Code | Activity | QTY | UOM | Hours / UOM | Subtotal Hours | Crew Loaded Rate ($/hr) | Subtotal Labor ($)
23 31 13 | Install galvanized rectangular duct (24ga) | 0 | SF | 0.18 |  | 68
23 31 13 | Install galvanized rectangular duct (20ga) | 0 | SF | 0.25 |  | 68
23 31 13 | Install round spiral duct | 0 | SF | 0.13 |  | 68
23 31 16 | Install stainless kitchen exhaust | 0 | SF | 0.45 |  | 68
23 31 19 | Install flex duct + connect | 0 | LF | 0.18 |  | 68
23 33 13 | Install volume damper | 0 | EA | 0.4 |  | 68
23 33 33 | Install fire damper (per UL system) | 0 | EA | 0.65 |  | 68
23 33 33 | Install smoke/combination damper | 0 | EA | 0.85 |  | 68
23 34 13 | Hang exhaust fan inline | 0 | EA | 1.5 |  | 68
23 34 13 | Set roof-mount exhaust fan | 0 | EA | 4.5 |  | 68
23 37 13 | Install supply diffuser | 0 | EA | 0.3 |  | 68
23 37 13 | Install return grille | 0 | EA | 0.25 |  | 68
23 37 13 | Install linear slot diffuser | 0 | EA | 0.65 |  | 68
23 21 13 | Install copper hydronic 3/4" - 1" | 0 | LF | 0.18 |  | 72
23 21 13 | Install copper hydronic 1-1/2" - 2" | 0 | LF | 0.32 |  | 72
23 21 13 | Install black steel hydronic 2" | 0 | LF | 0.35 |  | 72
23 21 13 | Install black steel hydronic 4" | 0 | LF | 0.65 |  | 72
23 21 13 | Install PEX-A hydronic 1" | 0 | LF | 0.08 |  | 72
23 21 23 | Set inline circulator pump | 0 | EA | 1.2 |  | 72
23 21 23 | Set base-mounted pump w/ flex connectors | 0 | EA | 4.5 |  | 72
23 21 23 | Set end-suction pump on housekeeping pad | 0 | EA | 6.5 |  | 72
23 21 29 | Install expansion tank | 0 | EA | 1.2 |  | 72
23 21 29 | Install air separator | 0 | EA | 1.5 |  | 72
23 05 23 | Install valve 1" - 2" | 0 | EA | 0.4 |  | 72
23 05 23 | Install valve 4" | 0 | EA | 0.85 |  | 72
23 05 23 | Install valve 6" + larger | 0 | EA | 1.5 |  | 72
23 11 23 | Install gas piping 1" black iron | 0 | LF | 0.35 |  | 72
23 11 23 | Install gas piping 2" black iron | 0 | LF | 0.52 |  | 72
23 62 23 | Install refrigerant pipe + insulate, 5/8" | 0 | LF | 0.25 |  | 74
23 62 23 | Install refrigerant pipe + insulate, 7/8" | 0 | LF | 0.35 |  | 74
23 62 23 | Refrigerant connection — brazed under N2 | 0 | EA | 0.85 |  | 74
23 07 13 | Insulate duct — fiberglass wrap | 0 | SF | 0.08 |  | 56
23 07 19 | Insulate pipe — 1" - 2" | 0 | LF | 0.12 |  | 56
23 07 19 | Insulate pipe — 4" + larger | 0 | LF | 0.2 |  | 56
23 36 16 | Set + connect VAV box (single-duct) | 0 | EA | 3.5 |  | 68
23 36 16 | Set + connect VAV box (fan-powered) | 0 | EA | 4.5 |  | 68
23 52 13 | Set 500-MBH boiler + connect | 0 | EA | 18 |  | 72
23 52 16 | Set 1500-MBH condensing boiler + connect | 0 | EA | 32 |  | 72
23 54 13 | Set + connect gas furnace 80 MBH | 0 | EA | 4.5 |  | 72
23 73 13 | Set indoor AHU + connect 3000 CFM | 0 | EA | 16 |  | 68
23 73 13 | Set indoor AHU + connect 8000 CFM custom | 0 | EA | 28 |  | 68
23 73 23 | Set rooftop unit 5 ton + connect | 0 | EA | 12 |  | 68
23 73 23 | Set rooftop unit 15 ton + connect | 0 | EA | 18 |  | 68
23 73 23 | Set rooftop unit 25 ton + connect | 0 | EA | 26 |  | 68
23 81 13 | Set fan coil unit + connect | 0 | EA | 4.5 |  | 72
23 81 23 | Set + connect mini-split indoor head | 0 | EA | 4.5 |  | 74
23 81 26 | Set + connect heat pump outdoor 4 ton | 0 | EA | 9.5 |  | 74
23 62 13 | Set DX split outdoor 3-5 ton | 0 | EA | 5.5 |  | 74
23 62 13 | Set VRF outdoor 10 ton | 0 | EA | 18 |  | 74
23 64 16 | Set chiller 60 ton air-cooled | 0 | EA | 28 |  | 72
23 65 13 | Set cooling tower 200 ton crossflow | 0 | EA | 40 |  | 72
23 72 13 | Set ERV 1000 CFM | 0 | EA | 12 |  | 68
23 09 13 | Install + commission VAV controller | 0 | EA | 2.5 |  | 78
23 09 13 | Install + commission AHU controller | 0 | EA | 8 |  | 78
23 09 33 | Install thermostat + connect | 0 | EA | 0.85 |  | 78
23 09 33 | Install duct sensor + connect | 0 | EA | 0.5 |  | 78
23 05 93 | TAB — supply air balance per outlet | 0 | EA | 0.5 |  | 70
23 05 93 | TAB — hydronic balance per circuit | 0 | EA | 1.2 |  | 70
23 08 00 | Cx — equipment functional test | 0 | EA | 4 |  | 78
23 08 00 | Cx — integration testing | 0 | LS | 16 |  | 78
[6 empty] | Productivity factor | 1
Labor Subtotal

## Equipment
EQUIPMENT ESTIMATE
Equipment | Days | Daily Rate ($) | Weeks | Weekly Rate ($) | Subtotal ($)
Sheet-metal brake / shear (rental) | 0 | 145 | 0 | 485
Threading machine 1" - 2" | 0 | 145 | 0 | 525
Pipe-bending machine — hydronic | 0 | 95 | 0 | 285
Refrigerant recovery machine + cylinders | 0 | 95 | 0 | 285
Vacuum pump — 2-stage 8 CFM | 0 | 65 | 0 | 195
Nitrogen tank + regulator | 0 | 35 | 0 | 105
Brazing torch + tank set | 0 | 45 | 0 | 145
Manifold gauge set + scale | 0 | 35 | 0 | 105
Hydronic flush kit | 0 | 95 | 0 | 285
Boom lift — 45' | 0 | 425 | 0 | 1485
Scissor lift — 19' | 0 | 145 | 0 | 485
Forklift — 5000 lb pneumatic | 0 | 285 | 0 | 985
Generator — 5kW portable | 0 | 65 | 0 | 195
Crane / rigging for heavy equipment lift | 0 | 1850 | 0 | 0
Office trailer (allocation) | 0 | 0 | 0 | 285
Truck / van allocation | 0 | 0 | 0 | 425
Equipment Subtotal

## Subcontract
SUBCONTRACT ESTIMATE
Scope (if subbed) | Vendor / Quote | Quote $ | Markup % | Subtotal ($)
Test, Adjust, Balance (TAB) — NEBB / AABC |  | 0 | 10%
Commissioning (Cx) — third-party CxA |  | 0 | 10%
BAS / DDC programming |  | 0 | 10%
Refrigerant charging + commissioning (EPA 608) |  | 0 | 10%
Boiler / chiller start-up — vendor |  | 0 | 5%
Insulation (if subbed) |  | 0 | 10%
Sheet-metal pre-fab (if subbed) |  | 0 | 10%
Crane / rigging — specialty heavy lift |  | 0 | 10%
Roof curbs + flashing |  | 0 | 10%
Hazmat / asbestos abatement (legacy MEP) |  | 0 | 10%
Concrete saw-cutting / core drilling |  | 0 | 10%
Hot-tap / live-cutover (gas / chilled water) |  | 0 | 10%
Subcontract Subtotal

## Premiums
PREMIUMS & CONDITIONS
Premium | Applies? (Y/N) | Adder % | Adder $ (overrides %)
Prevailing wage | N | 15% | 0
Occupied building / live-cutover | N | 10% | 0
Hospital ICRA tier 3+ | N | 10% | 0
Heights > 14 ft (lift / crane) | N | 5% | 0
Roof-top set requiring crane lift | N | 6% | 0
Tight mechanical room (extended labor) | N | 5% | 0
Hazardous-area (refrigerant + flammable) | N | 6% | 0
After-hours / weekend / night shift | N | 20% | 0
Travel / per diem | N | 3% | 0
Winter / cold-weather working | N | 4% | 0
LEED / Cx documentation | N | 4% | 0
Owner-direct equipment (no markup) | N | -10% | 0
Premium $ total (applies-Y only)
Premium % total (applies-Y only)

## CSI Reference
CSI MASTERFORMAT — DIVISION 23 HEATING / VENTILATING / AIR-CONDITIONING
23 00 00 | HEATING, VENTILATING, AND AIR-CONDITIONING (HVAC)
23 05 00 | Common Work Results for HVAC
23 05 13 | Common Motor Requirements for HVAC Equipment
23 05 17 | Sleeves and Sleeve Seals for HVAC Piping
23 05 19 | Meters and Gauges for HVAC Piping
23 05 23 | General-Duty Valves for HVAC Piping
23 05 29 | Hangers and Supports for HVAC Piping and Equipment
23 05 53 | Identification for HVAC Piping and Equipment
23 05 93 | Testing, Adjusting, and Balancing for HVAC
23 07 00 | HVAC Insulation
23 07 13 | Duct Insulation
23 07 19 | HVAC Piping Insulation
23 08 00 | Commissioning of HVAC
23 09 00 | Instrumentation and Control for HVAC
23 09 23 | Direct-Digital Control System for HVAC
23 09 33 | Electric and Electronic Control System for HVAC
23 11 23 | Facility Natural-Gas Piping
23 21 13 | Hydronic Piping
23 21 16 | Hydronic Piping Specialties
23 21 23 | Hydronic Pumps
23 22 13 | Steam and Condensate Heating Piping
23 25 13 | Water Treatment for Closed-Loop Hydronic Systems
23 31 13 | Metal Ducts
23 31 16 | Nonmetal Ducts (fabric, FRP)
23 31 19 | HVAC Casings
23 33 13 | Dampers
23 33 19 | Duct Silencers
23 33 33 | Air-Duct Accessories — Fire Dampers, Smoke Dampers
23 34 13 | Axial HVAC Fans
23 34 16 | Centrifugal HVAC Fans
23 36 16 | Variable Air Volume Boxes (VAV)
23 37 13 | Diffusers, Registers, and Grilles
23 41 00 | Particulate Air Filtration
23 52 13 | Hot-Water Boilers
23 52 39 | Electric Boilers
23 54 13 | Gas Furnaces
23 57 13 | Heat Exchangers for HVAC
23 62 13 | Packaged Compressor and Condenser Units
23 62 23 | Refrigerant Piping
23 64 16 | Air-Cooled Chillers
23 64 19 | Water-Cooled Chillers
23 65 13 | Cooling Towers
23 72 13 | Air-to-Air Energy Recovery Equipment (ERV / HRV)
23 73 13 | Indoor Central-Station Air-Handling Units
23 73 23 | Packaged Outdoor HVAC (Rooftop)
23 81 13 | Fan-Coil Units
23 81 23 | Computer-Room Air Conditioners (CRAC / CRAH)
23 81 26 | Heat Pumps — Air-Source
23 83 13 | Radiant Heating
22 13 / 22 14 | Plumbing — sanitary / storm (cross-ref)
26 27 / 26 28 | Electrical — power + disconnects to HVAC equipment (cross-ref)
27 21 / 27 22 | BAS Communications (cross-ref)