Ductwork — Gauge Selection (SMACNA)

Duct Reinforcement + Joint Selection

Duct Support Spacing

Duct Sealing + Leakage Class

Duct Leakage Testing (SMACNA DCS)

Hydronic Piping — Material + Hanger Spacing

Hydronic Pressure Testing + Flush + Fill

Gas Piping (IFGC 406)

Steam + Condensate

Acceptance Documentation

Per SMACNA HVAC Duct Construction Standards. Gauge depends on duct dimension, pressure
    class (1 in wg, 2 in wg, 4 in wg, 6 in wg, 10 in wg), and seismic + service.

| Pressure Class | Max Static (in wg) | Typical Application |
| --- | --- | --- |
| 1 in wg (low) | 1.0 | Most return + low-velocity supply |
| 2 in wg | 2.0 | Typical commercial supply |
| 4 in wg | 4.0 | High-velocity / long-run supply |
| 6 in wg | 6.0 | Process / industrial |
| 10 in wg | 10.0 | High-volume process |

SMACNA tables provide reinforcement type + spacing based on gauge + pressure class.

Joints: TDC, TDF, slip-and-drive, S-cleat — match SMACNA T-classification.

Seal class — A (all transverse + longitudinal + penetrations), B (transverse +
            longitudinal), C (transverse only).

Sealant — UL 181A (rigid duct) or UL 181B (flex). Approved tape only — duct tape
            (cotton fabric) NOT approved.

Per SMACNA. General rules — vary by gauge + size.

| Duct Size (largest dimension) | Max Hanger Spacing | Hanger Material (typical) |
| --- | --- | --- |
| Up to 30" | 10 ft horizontal | 1" × 18ga strap or 3/8" rod |
| 31" - 60" | 10 ft horizontal | 1.5" × 16ga strap or 3/8"-1/2" rod |
| 61" - 96" | 8 ft horizontal | 1.5" × 14ga strap or 1/2" rod |
| Over 96" | per SMACNA + EOR | Engineered support |
| Vertical riser | Per story / 12 ft min | SMACNA bracket schedule |

| Pressure Class | Seal Class | Leakage Class CL (cfm/100sf at 1" wg) |
| --- | --- | --- |
| ≤2 in wg, return | B (transverse + longitudinal) | CL 12 (12 cfm/100sf) |
| ≤2 in wg, supply | A (all joints sealed) | CL 6 |
| 3-4 in wg | A | CL 6 |
| 6+ in wg | A | CL 3 |

Required by IECC 2021 and many spec sections for ducts in unconditioned spaces.

Apparatus: calibrated fan, orifice or flow meter, manometer, pressure tap.

Isolate the duct section + cap all openings.

Pressurize to test pressure (typically equal to design static).

Measure leakage at the test pressure.

Calculate CL = leakage cfm × 100 / total surface area sq ft.

Pass if measured CL ≤ specified CL.

Document on the Pressure + Leakage Test Log.

| Material | Pipe Size | Horizontal Spacing |
| --- | --- | --- |
| Copper Type L | 1/2" - 1" | 6 ft |
| Copper Type L | 1-1/4" - 2" | 8 ft |
| Copper Type L | 2-1/2" - 4" | 10 ft |
| Black Steel | 1" - 2" | 10 ft |
| Black Steel | 2-1/2" - 4" | 12 ft |
| Black Steel | 5" - 8" | 14 ft |
| PEX-A (oxygen barrier) | 1/2" - 1" | 32" (per most mfrs) |

Pressure test — typical 1.5 × working pressure or 100 psi minimum.
            Hold 1 hour for sub-50 psi systems; longer for larger systems per spec. No pressure
            loss permitted.

Flush — full system flush to dislodge debris BEFORE filling. Flushing
            water bypasses sensitive components (coils, control valves). Flush to clear.

Chemical treatment / glycol — fill with treated water or glycol blend
            per spec. Chemical addition with pot feeder.

Air venting — air-vent at every high point during fill + final purge.

Cross-connection — RPZ at make-up. Document on plumbing's Backflow Test Log.

Closed-loop water analysis — sample + lab analysis at commissioning for
            glycol concentration + chemical inhibitor levels.

Black iron (Schedule 40) or CSST (with arc-bonding per CSST listing).

Sizing per IFGC Table 402 or NFPA 54.

Drip leg + sediment trap at each appliance.

Shutoff valve within 6 ft of each appliance.

Test pressure: 3 psi minimum for 2-psi systems; 1.5× working pressure higher.

Test duration: 10 minutes minimum on small systems; longer for larger.

Test medium: air or nitrogen — NEVER fuel gas for testing.

Soap-test every joint. Witness by AHJ inspector.

Schedule 40 black steel typical. Schedule 80 for high-pressure.

Welded or threaded per pressure class. ASME B31.9 power-piping rules apply at higher
            pressures.

Pitch toward drip legs + traps; condensate gravity drainage to receiver.

Traps: F&T (float + thermostatic) for steady drainage; thermostatic for radiant.

Strainer upstream of each trap.

Pressure test: hydrostatic 1.5× working (typically); pneumatic only with engineering
            sign-off + safety provisions.

Insulation per ASHRAE 90.1 + spec.

Pressure test logs on each system (duct, hydronic, gas, steam, refrigerant).

Leakage test reports (duct CL calculation).

Flush + chemical treatment records (hydronic).

Vacuum decay results (refrigerant — to 500 micron decay test).

Equipment startup forms by manufacturer's tech.

Photos of every penetration / firestop before cover.

As-built redlines current with field deviations.

Submit per spec — typically pre-final inspection.