EPA 608 Certification Levels

Refrigerant Classifications (ASHRAE 34)

Recovery + Recycling + Reclaim

Leak Detection + Repair Requirements

ASHRAE 15 Machinery Room Requirements

A2L Refrigerant Protocols

Brazing Under Nitrogen — Step-by-Step

Hot Work Permit + Fire Watch

Hose + Cylinder Handling

Documentation Requirements

| Type | Scope | Examples |
| --- | --- | --- |
| Type I | Small appliance (≤5 lb refrigerant) servicing | Domestic refrigerator, vending machine |
| Type II | High-pressure appliance servicing | Most commercial HVAC, R-410A, R-32, R-454B |
| Type III | Low-pressure appliance servicing | R-123 centrifugal chillers |
| Universal | All three above | — |

Every technician opening a refrigerant circuit needs the appropriate certification.
    Document cert + expiry on the Refrigerant Log. Disposing of refrigerant without recovery is a
    Clean Air Act §608 violation — fines per incident plus possible criminal liability.

| Class | Definition | Examples |
| --- | --- | --- |
| A1 | Low toxicity, no flame propagation | R-410A, R-134a, R-22 (legacy) |
| A2L | Low toxicity, mildly flammable (LFL > 3.5%, BV < 10 cm/s) | R-32, R-454B, R-1234yf, R-1234ze |
| A2 | Low toxicity, flammable | R-152a |
| A3 | Low toxicity, higher flammability | R-290 (propane), R-600a (isobutane) |
| B1 | Higher toxicity, no flame propagation | R-123 (low-pressure) |
| B2L / B2 / B3 | Higher toxicity, flammable variants | R-717 (ammonia) — B2L |

Recovery — remove refrigerant from a system into a DOT-rated recovery cylinder
            using an EPA-certified recovery machine. EPA-required pressure levels:
            
High-pressure ≥15 hp: 10 in Hg vacuum.
High-pressure <15 hp: 0 psig.
Low-pressure: 25 mm Hg absolute (29 in Hg vacuum).

Recycle — clean refrigerant on site using a recycler; suitable for return to
            same equipment.

Reclaim — send to a certified reclamation facility; brings refrigerant to
            ARI-700 purity for resale.

Cylinder labels — yellow top for recovery; never refill virgin cylinders
            with recovered refrigerant.

Disposal — through certified reclaimer; never vent.

Log each recovery on the Refrigerant Log: date, equipment, lbs recovered, cylinder ID.

EPA Section 608 (Subpart F) requires leak repair on systems with charge ≥50 lb in commercial
            applications. Annual leak rate triggers:
            
Commercial refrigeration >30% annual leak → repair required.
Comfort cooling >10% annual leak → repair required.

Leak detection methods: electronic detector (most sensitive), bubble (soap) test, UV dye + lamp.

Verify repair via initial verification test (within 30 days) + follow-up (within 30 days).

Document each leak event + repair + verification on the Refrigerant Log.

Refrigerant management plan required for facilities with multiple systems.

Machinery rooms housing refrigeration equipment must meet ASHRAE 15 requirements:

Refrigerant detection — sensor + alarm at concentration thresholds (typically 25%
            of RCL or per local code).

Mechanical ventilation — interlocked with detector; minimum cfm per ASHRAE 15 formula.

Emergency stop / shut-off — readily accessible at exit door.

Egress — minimum two means of egress on opposite walls for rooms above threshold size.

Self-contained breathing apparatus (SCBA) — required outside the door for class B
            refrigerants and A2L in many cases. Verify per local code.

Labels — refrigerant type + amount posted at room entrance.

LFL detection in installation areas (refrigerant-specific sensor).

Leak-tight commissioning + pressure test before charging.

Charge limits per ASHRAE 15 + IMC 2024 Section 1106 (varies by occupancy + room size).

NO ignition sources within the installation envelope during brazing.

Brazing on dedicated refrigerant lines OK with proper nitrogen purge + post-braze leak test.

Training documentation — every tech touching A2L systems trained + competency-tested.

Verify line is recovered + isolated.

Connect nitrogen regulator + flow meter; set 5-10 SCFH.

Crack open opposite end so nitrogen can flow through.

Apply heat + braze filler. BCuP-2 or BAg alloy as spec'd.

Maintain nitrogen flow during cool-down (slow cooling = scale-free interior).

Pressure test post-braze: nitrogen pressurize per spec (commonly 150-500 psig depending on
            high/low side); soap-test every joint; hold for spec'd duration.

Vacuum to 500 microns; hold per spec (typically 15 min decay test < 500 microns).

Charge to spec.

Verify subcool / superheat per equipment data plate.

Document each step on the Refrigerant Log.

Hot Work Permit required for brazing, welding, soldering, grinding, cutting.

Permit issued daily by GC (or qualified site safety person).

Clear 35 ft of combustibles or cover with welding blankets / FR tarps.

Sweep up combustible dust + lint within radius.

Fire watch present during work + 30-min cool-down (60 min in some jurisdictions).

Fire extinguisher (A + B + C) within 10 ft.

Smoke-detector + sprinkler isolation coordinated + restored before leaving.

Outdoor wind — cease at > 15 mph wind / dust events.

NEVER hot work near refrigerant cylinders or open A2L refrigerant systems without LFL clearance.

Hoses rated for the refrigerant + pressure.

Self-sealing connectors (low-loss fittings) — avoid venting on disconnect.

Cylinders secured upright; never lay-down a recovery cylinder during use.

Cylinder weight checks — verify recovery cylinder not over 80% fill (DOT requirement).

Outdoor storage — direct sunlight + heat increases pressure; shade + ventilate.

DOT marking compliance: USDOT-rated cylinders only; never use disposable cylinders for recovery.

Transport — secured + placarded per DOT 49 CFR 173.

Per-tech EPA 608 certification on file + on site.

Per-event recovery log: date, equipment, lbs in, lbs out, cylinder ID.

Leak detection + repair log per Subpart F.

Hot Work Permit log + signed permits archived per project.

Nitrogen pressure test results + vacuum decay logged per system.

Final refrigerant charge documented (equipment data plate + service tag).

EPA refrigerant management plan for facilities with multiple systems above threshold.