This Site-Specific Mechanical Plan ("SSMP") is the mechanical contractor's project-specific
        compliance roadmap covering AHJ coordination, the inspection sequence, refrigerant handling
        (EPA 608), hot work + brazing, lifting + rigging of heavy equipment, confined-space entry
        in mechanical rooms, hazmat encountered, ICRA / occupied-building considerations, and
        multi-trade coordination. Walk it with the GC + AHJ inspector at pre-construction; sign at
        Section 16. OSHA Multi-Employer Citation Policy applies — GC + mech contractor jointly
        citable.

Parties & Project Identification

Permits, AHJ & Code Edition

Inspection Sequence (UG / Rough / Equipment / Final)

Mechanical Scope of Work

Refrigerant Handling (EPA 608) + ASHRAE 15 Compliance

Hot Work — Brazing, Welding, Soldering

Confined-Space Entry (Mech Rooms / Plenums)

Heavy Equipment Lifting + Rigging

Working at Heights (Roof Units, Mech Penthouses)

Hazmat Encountered (Asbestos / Lead / Mold)

Indoor Air Quality + Construction-Phase IAQ (ASHRAE 62.1)

Multi-Trade Coordination

Occupied-Building / ICRA / Live-Cutover

TAB + Commissioning Touchpoints

Emergency Response + Stop-Work Triggers

Signatures

| Project Name | [Project] |
| --- | --- |
| Owner | [Owner + Rep] |
| General Contractor | [GC + Project Manager] |
| Mechanical Engineer of Record | [MEP firm + EOR] |
| Mechanical Contractor | [Contractor Legal Name] |
| State License # | [# + Master Mech of Record] |
| Mechanical Superintendent | [Name + Phone] |
| Sheet-Metal Foreman | [Name + Phone] |
| Pipefitter Foreman | [Name + Phone] |
| Refrigeration Lead (EPA 608) | [Name + cert #] |
| Total Tonnage | [T] |
| Total Supply CFM | [CFM] |

| Mechanical Permit # | [#] |
| --- | --- |
| Gas Piping Permit (if separate) | [#] |
| AHJ — Mechanical Inspector | [Name + Cell] |
| Adopted Mechanical Code | [IMC 2024 / UMC 2024 / local] |
| Adopted Energy Code | [IECC 2021 / ASHRAE 90.1-2019] |
| Adopted Fuel Gas Code | [IFGC 2024 / NFPA 54] |
| Adopted Ventilation Standard | [ASHRAE 62.1] |
| Adopted Refrigeration Standard | [ASHRAE 15] |
| EPA 608 Certification | [Tech name + cert level + exp] |

| Inspection | Trigger | What Gets Inspected |
| --- | --- | --- |
| UG / In-Slab | Pre-pour | Refrigerant line sleeves, hydronic UG piping, gas service entry, condensate stub-outs |
| Rough-In | Pre-drywall | Ductwork seismic + support, sealed joints, fire/smoke damper UL listing, hydronic + gas piping support spacing, condensate slope |
| Pressure / Leak Tests | Pre-cover | Gas (IFGC 406), hydronic 1.5× working OR 100 psi, refrigerant nitrogen pressure test, ductwork leakage per SMACNA |
| Equipment Set | After rigging | Anchor + seismic restraints, vibration isolators, clearance + service access, T&P piping, code venting |
| TAB + Cx | Pre-final | Air + water balance reports, sequence-of-ops verification, integration testing |
| Final | Pre-TCO | Filters installed, all systems labeled, all required filters / dampers operative, IAQ flush-out documented if required |

| CSI Code | System | Scope |
| --- | --- | --- |
| 23 05-09 | Common Work + Insulation + Controls | BY US |
| 23 21 | Hydronic Piping + Pumps | BY US |
| 23 22 | Steam + Condensate | [scope] |
| 23 31-37 | Ductwork + Accessories + Air Outlets | BY US |
| 23 52-57 | Boilers + Heat Exchangers | [scope — start-up by vendor?] |
| 23 62-65 | DX + Chillers + Cooling Towers | [scope] |
| 23 72-73 | ERV + AHU + RTU | [scope + crane lifts] |
| 23 81-83 | Unitary HVAC + Radiant | [scope] |
| 22 13/22 14 | Plumbing — sanitary / storm (cross-ref) | BY OTHERS |
| 26 27-28 | Electrical — power to mech equipment | BY OTHERS — final-connection scope split |
| 27 21 | BAS / Controls integration | [BY US / specialty sub] |

Technician certification — EPA 608 Type II (high-pressure systems) or
            Type III (low-pressure) required for any refrigerant work. Universal cert covers all.
            Document each tech's cert + expiry.

Recovery — recover refrigerant to EPA standards before opening any system.
            Use certified recovery machine + DOT-rated cylinders. Log recovery on Refrigerant Log.

Leak detection — required after any service work; use electronic detector,
            soap test, OR refrigerant trace.

ASHRAE 15 — refrigerant classification (A1, A2L, A3, etc.) + machinery
            room ventilation per Standard 15.

Refrigerant labeling — equipment labeled with refrigerant type +
            amount per ASHRAE 15.

R-410A + replacements — confirm phase-down schedule + EPA SNAP listing
            for project HVAC refrigerant.

Daily Hot Work Permit from GC. Don't pre-pull.

35-ft combustible clearance + welding blankets / FR tarps on remainder.

Fire watch during work + 30-min cooldown (60 min some AHJs).

Fire extinguisher (A + B + C) within 10 ft.

Verify smoke detector status with GC; restore by end of shift.

Brazing under nitrogen — required on refrigerant + medical-gas piping.
            5-10 SCFH nitrogen purge during entire braze. Prevents scale inside pipe.

Welder qualification — pipe welding per ASME Section IX where applicable.
            Joint testing per spec.

Mechanical rooms + plenum chases often qualify as confined spaces or permit-required
            confined spaces (PRCS) — limited entry/exit + atmospheric hazards (refrigerant leaks,
            fuel-gas, combustion products from gas-fired equipment).

Atmospheric test before entry: oxygen → flammable → toxic.

Continuous ventilation if combustion equipment is operating during the entry.

Permit + entry supervisor + attendant + rescue per 1910.146.

Retrieval system unless retrieval would increase risk.

Rooftop units, AHUs, chillers — typically craned. Coordinate with GC's crane plan +
            ground-bearing analysis.

Critical-lift criteria: load > 75% of crane capacity, lifts over occupied buildings,
            lifts of expensive / irreplaceable equipment.

Rigging — synthetic slings inspected, choker hitches per OSHA 1926.251, tag lines for
            wind control.

Roof access — fall protection per 1926.501.

Lift area cleared of personnel + barricaded.

Operator certification — crane operators must be certified per 1926.1427.

Fall protection > 6 ft (construction) — 1926.501.

Mechanical equipment on rooftops without parapet → fall-arrest tie-off or warning-line
            system.

Aerial lift training + daily inspection.

Material lift to roof — coordinate with crane / hoist; don't carry heavy items on ladders.

Asbestos in pipe insulation (pre-1980) — STOP, isolate, abatement vendor.

Lead-based paint on legacy ductwork — RRP-certified renovator if pre-1978.

Mold in damp coils / drain pans — clean + remediate per IICRC S520 before
            new work.

PCBs in old transformers serving mech equipment — confirm w/ EC before
            disturbance.

Mercury — old fluorescent ballasts on legacy AHUs.

ASHRAE 62.1 ventilation rates — verify at TAB. Increase OA per Table 6.1 if missed at
            design.

Construction-Phase IAQ Management Plan (LEED IEQc3 / SMACNA IAQ Guidelines)
            — protect installed ductwork during construction; cap open ends; HEPA-vacuum before final.

Pre-occupancy flush-out — minimum 14,000 ft³ of OA per ft² of floor area BEFORE
            occupancy if LEED IEQc3.2.

Filter replacement — install permanent MERV filters AFTER flush-out + before turnover.

Document IAQ plan compliance for LEED / WELL projects.

BIM coordination — Mechanical typically priority above ceiling after structure +
            gravity (sanitary / storm). Coordinate with sprinkler mains + electrical conduit.

Sleeves + roof curbs coordinated with structural + roofing.

Power to mech equipment — confirm scope split with EC.

Control wiring — confirm scope with BAS sub.

Floor sleeves through occupied areas — coordinate with arch / interiors.

Hospital ICRA tier 3+ — HEPA negative-pressure containment for any work
            disturbing existing duct or piping. Coordinate with IP.

Live-cutover — written plan + occupant notification + temporary ventilation
            during shutdown. Coordinate with owner ops.

Steam / chilled water cutovers — isolate, drain, lock + tag. Test for
            zero pressure before opening.

Refrigerant leak in occupied area — evacuate + ventilate per ASHRAE 15
            machinery room protocols.

Pre-TAB clean filter set installed; final filters per spec.

TAB by NEBB-certified or AABC-certified firm. Use the project TAB report template.

Sequence-of-Operations review with controls + EOR before integration test.

Functional Performance Tests (FPT) per Cx spec.

Integrated systems test if multiple subsystems handed over together.

Document deficiencies + retest after correction.

| Site First-Aid / AED | [location] |
| --- | --- |
| Nearest Hospital + ER | [name + drive time] |
| Refrigerant Emergency Vendor | [24-hr phone] |
| Gas Emergency | [Utility 24-hr] |
| Hazmat Vendor | [24-hr] |

Suspected asbestos / lead / mold disturbed.

Refrigerant leak in occupied space.

Gas leak detected at any concentration.

Confined-space entry without permit.

Hot work without permit / fire watch.

Crane lift exceeds 75% capacity or weather thresholds exceeded.

Code-edition conflict between drawings and AHJ adopted code.

Pressure-test failure that cannot be promptly diagnosed.

A2L refrigerant work without LFL monitoring.

Worker injury exceeding first-aid level.

Revision history: log each substantive change. Post current version at jobsite.