TAB vs Cx — Roles + Sequence

TAB Methodology (NEBB / AABC)

Air-Side TAB Procedures

Water-Side TAB Procedures

Cx Authority (CxA) Process per ASHRAE Guideline 0

Sequence of Operations Review

Functional Performance Tests (FPT)

Integrated Systems Test

Deficiency Log + Re-Test

Final Reports + Owner Training

|  | TAB | Commissioning (Cx) |
| --- | --- | --- |
| Purpose | Measure + adjust airflows, water flows, and pressures to match design | Verify systems function per Owner's Project Requirements (OPR) + Basis of Design (BOD) |
| Performer | NEBB or AABC certified firm (typically a sub) | Cx Authority (CxA) — owner-direct, independent of mech contractor |
| Reference Standard | NEBB Procedural Standard / AABC National Standard | ASHRAE Guideline 0 (overall Cx process), ASHRAE Guideline 1.1 (HVAC Cx) |
| Timing | Pre-substantial; after install + before final inspection | Spans design through 12-month post-occupancy |
| Output | TAB report with as-measured values | Cx report — FPT results, deficiency log, training records |

Mechanical install complete + pressure tested + filters installed.

Pre-functional checklists (PFC) — installer verifies + signs each piece of equipment.

Equipment start-up — manufacturer's tech where required.

Air-side TAB — measure + adjust supply / return / exhaust flows.

Water-side TAB — measure + adjust hydronic flows.

Sequence of Operations (SoO) review with CxA + EOR + controls.

Functional Performance Tests (FPT) — system + integrated.

Deficiency correction + re-test.

Owner training + O&M handover.

12-month seasonal verification (cooling + heating).

NEBB-certified or AABC-certified firm (verify cert + project-specific TAB technician
            cert).

Instrument calibration current — required on every project. Verify cal sticker.

Pre-TAB inspection: filters installed (clean), dampers open, system per design.

TAB report template per NEBB / AABC standard.

Project-specific tolerance — typically ±10% of design value for airflow, ±5% for
            water flow (verify spec).

Start at the AHU/RTU: total supply + return + OA airflows. Adjust at unit volume control or
            VFD to reach design.

Trunk + main branches — Pitot traverse where access permits. Measure velocities → calculate cfm.

Terminal units (VAV / FCU) — measure inlet + adjust min/max settings.

Diffusers + grilles — hood capture method or Alnor traversing. Adjust dampers to
            distribute design cfm.

Re-balance trunk + main after diffusers — minor iteration.

Outdoor air (OA) — verify per fixed minimum or DCV setpoint.

Exhaust flows — kitchen, lab, bathroom, parking ramp.

Pressure relationships — building, room, lab — measured + recorded.

Document each terminal + each piece of equipment on TAB Air-Side Log.

Pump GPM + head — measure at design + verify against pump curve.

Riser flows — adjust via balancing valves to design.

Coil flows — measure via P-T plugs + pressure-drop or via balancing-valve gauge.

Boiler + chiller — verify delta-T per design.

Cooling tower — verify approach + range.

Document on TAB Water-Side Log.

OPR — Owner's Project Requirements document (often by CxA).

BOD — Basis of Design (by EOR).

Design Review — CxA reviews design against OPR.

Cx Plan — issued by CxA at construction start. Includes Cx schedule,
            equipment list, FPT scope, training plan.

Installation Verification — Pre-Functional Checklists (PFC) by installer +
            verified by CxA.

FPT — Functional Performance Tests per equipment + system.

Integrated Systems Test — multi-system test (life-safety + smoke + HVAC integration).

Training + Documentation — owner training; final Cx report; warranty period
            follow-up.

Seasonal Verification — opposite-season testing (typically 9-12 months post).

Review SoO from BAS submittal with CxA + EOR + controls before FPT.

Each operating mode (occupied / unoccupied / warm-up / setback / morning-warm-up / smoke
            mode / fire-alarm) — define triggers + expected response + override behavior.

Setpoints + dead-bands documented.

Alarm thresholds + escalation defined.

BAS graphics + point lists reviewed for completeness.

Owner-facing dashboards reviewed.

Equipment-specific FPT — each AHU, RTU, chiller, boiler, pump, fan, VFD per spec template.

Stepwise tests: start, run at min/normal/max output, stop, alarms, BAS reporting.

Verify safeties — low-temp cutout, smoke detector trip, freeze stat, high-static cut-out.

Verify staging on multi-piece equipment (lead-lag, alternation).

Verify control-loop response (no hunting, stable PID).

Document on FPT Log; deficiency → re-test after correction.

Integration of multiple systems: HVAC + fire alarm + smoke control + life-safety.

Test smoke-mode response: smoke detector trips → HVAC shutdown + dampers operate +
            stairwell pressurization.

Test fire-alarm interface: dampers close, emergency exhaust starts, AHUs shut down per SoO.

Test power-loss + emergency restoration: equipment restart sequence per SoO.

Witness by CxA + AHJ where required by life-safety code.

Document on Integrated Test Log.

Log every deficiency identified during FPT / IST.

Assign owner + due date.

Re-test after correction; don't simply mark "done."

Open deficiencies → withhold from substantial completion sign-off.

Categorize by severity: punch (cosmetic), functional (impacts operation), critical
            (impacts safety / OPR compliance).

TAB Final Report — by NEBB / AABC firm. Includes as-measured values for every
            terminal + equipment + system pressure.

Cx Final Report — by CxA. Includes OPR + BOD, FPT results, deficiency log
            closeout, training records, recommendations.

Owner Training — typically 8+ hours covering system overview, sequence of
            operations, BAS interface, alarms, routine maintenance. Documented with sign-in sheet.

O&M Manual integration — TAB + Cx reports become part of O&M manual.

Warranty period — Cx-tracked deficiencies addressed under warranty;
            12-month seasonal verification typical.