## Instructions
BACKFLOW TEST LOG — INSTRUCTIONS
PURPOSE
Per-device test record for every backflow-prevention device on a project. Captures
initial test (after installation, before service), annual tests (12-month intervals),
and repair history. Submission-ready format for water purveyor + local AHJ.
WORKFLOW
1. Device Inventory — list every backflow device on the project at install time.
Assign an owner-defined Device ID for the column. Include make / model / size /
serial / location.
2. Initial Test Log — one row per device, completed by state-licensed tester after
install + before placing system in service. All three test readings recorded.
3. Annual Test Log — recurring annual record. Same tester licensure required.
4. Repair Log — any failure leading to a repair or replacement. Drives traceability.
5. Reporting Summary — pulls test status by device for the building owner + AHJ.
TEST READINGS — WHAT EACH NUMBER MEANS
Check #1 differential — pressure across the upstream check (RPZ + DCV). Pass:
≥1.0 psid (RPZ); ≥1.0 psid (DCV).
Relief Opening — RPZ only. Pressure at which the relief valve opens during the
upstream-isolation test. Pass: ≥2.0 psid.
Check #2 held — DCV + RPZ. Verifies #2 holds against zero downstream pressure.
Pass: visible hold for the test duration.
REQUIRED CALIBRATION
Test gauges must be calibrated within the prior 12 months. Record the gauge serial
number + calibration date on every test row. AHJs reject tests with out-of-cal gauges.
REPORT SUBMISSION
Most jurisdictions require submission within 10 days of testing. Send to: (1) building
owner / facility manager, (2) water purveyor, (3) local AHJ plumbing inspector.
Confirm specific submission requirements with each entity at the initial install.
OUT-OF-SERVICE PROTOCOL
A failed device must be tagged ('OUT OF SERVICE — DO NOT USE'), the owner notified in
writing within 24 hours, and repaired or replaced within 30 days. Document the tagging
+ notification in the Repair Log.
DOCUMENT VERSION
Backflow_Test_Log.xlsx v1.0 — 2026-05-19
ContrPro Complete Tier · Plumbing Trade Pack

## Device Inventory
DEVICE INVENTORY
Device ID | Location (Bldg/Room) | Application | Type (RPZ/DCV/PVB/AG) | Size | Make / Model | Serial # | Install Date

## Initial Test Log
INITIAL TEST LOG (after install, before service)
Device ID | Test Date | Tester Name | Tester License # | Gauge Serial | Gauge Cal Date | Check #1 (psid) | Relief Open (psid, RPZ) | Check #2 Held | Pass / Fail | Notes

## Annual Test Log
ANNUAL TEST LOG
Device ID | Test Date | Tester Name | Tester License # | Gauge Serial | Gauge Cal Date | Check #1 (psid) | Relief Open (psid, RPZ) | Check #2 Held | Pass / Fail | Notes

## Repair Log
REPAIR LOG
Device ID | Fail Date | Symptom | Cause Identified | Repair Performed | Repaired By | Re-test Date | Re-test Pass / Fail | Owner Notified (Date)

## Reporting Summary
REPORTING SUMMARY (informational)
Device ID | Application | Last Test Date | Next Test Due | Status | Sent To (Purveyor / AHJ / Owner)