## Instructions
PRESSURE TEST LOG — INSTRUCTIONS
PURPOSE
Captures every pressure / leak test performed on the project — hydrostatic water,
DWV (sanitary + storm), and natural gas. Submission-ready format for the AHJ
plumbing inspector and the project closeout binder.
WHEN TO LOG A TEST
• Underground / in-slab — BEFORE backfill or slab pour
• Above-ground rough — BEFORE drywall closes the assembly
• Top-out stack test — DWV system pressurized for final
• Gas pressure test — BEFORE any appliance is connected + before AHJ witness
• Re-test after any repair or modification to a previously-tested assembly
WHAT TO RECORD
• Test date + time + duration
• System tested + area (floor / building / wing)
• Test pressure + medium (water / air / nitrogen)
• Start + finish gauge readings
• Gauge serial # + calibration date
• Tester name + signature
• Witness (AHJ inspector / GC superintendent) — name + signature if applicable
• Pass / fail + remarks
FAILED-TEST PROTOCOL
Document failure in the Failed-Test Investigation Log tab. Identify the leak,
perform the repair, re-test, and re-document. Don't 'erase' a failed test —
the inspection trail is part of the QC system.
GAUGE CALIBRATION
Test gauge must read in the middle third of its scale at the test pressure (e.g.
use a 0-100 psi gauge for a 50 psi test, not a 0-1000 psi gauge). Gauge must have
calibration within prior 12 months — record cal date + cal lab on every test row.
DOCUMENT VERSION
Pressure_Test_Log.xlsx v1.0 — 2026-05-19
ContrPro Complete Tier · Plumbing Trade Pack

## Test Schedule
TEST SCHEDULE (planned)
System | Area / Floor | Planned Date | Test Type | Pressure | Medium | Status

## Hydrostatic Test Log
HYDROSTATIC TEST LOG — DOMESTIC WATER + STORM
Test ID | System (CW / HW / Recirc / Storm) | Area / Floor | Test Date | Test Time | Test Pressure (psi) | Start (psi) | Finish (psi) | Hold (min) | Gauge Serial / Cal Date | Tester | Pass / Fail | Notes

## DWV Test Log
DWV TEST LOG — SANITARY + STORM (Air or Water Head)
Test ID | System (Sanitary / Storm) | Area / Floor | Test Date | Test Time | Method (Water Head / 5 psi Air) | Hold (min) | Gauge Serial / Cal Date | Cap Failures Noted | Tester | Pass / Fail | Notes

## Gas Pressure Test
GAS PRESSURE TEST LOG (IFGC 406 / NFPA 54)
Test ID | System (NG / LP) | Area / Floor | Test Date | Test Time | Test Pressure (psi) | Start (psi) | Finish (psi) | Hold (min) | Gauge Serial / Cal Date | Test Medium (Air / N2) | Tester / License # | Pass / Fail + Notes

## Failed-Test Investigation
FAILED-TEST INVESTIGATION LOG
Test ID (failed) | Date | Failure Mode | Leak Location Found | Cause | Repair Performed | Re-test Date | Re-test Result

## Reporting Summary
REPORTING SUMMARY (informational)
System Category | Tests Planned | Tests Performed | Tests Passed | % Complete
Hydrostatic — Domestic Water | 0 | 0 | 0
Hydrostatic — Storm | 0 | 0 | 0
DWV — Sanitary | 0 | 0 | 0
DWV — Storm | 0 | 0 | 0
Gas Pressure | 0 | 0 | 0
Other | 0 | 0 | 0