Closeout Timeline (3 Phases)

Final Inspection — What the AHJ Looks For

Punch List Management

Substantial vs Final Completion

O&M Manual Contents

As-Built Drawings

Warranty Period & Documentation

Required Submissions to Owner / AHJ / Purveyor

Lien Releases & Retention

Common Closeout Pitfalls

Walk every system with the foreman. Self-punch before the GC walk.

Verify every backflow device has an Initial Test report on file.

Verify disinfection report on file with chain-of-custody.

Complete all final inspections; clear any open AHJ correction notices.

Submit pre-final O&M manual draft for owner review.

Verify as-built redlines current at each foreman + uploaded to project shared drive.

Owner / GC walk + punch list issued.

Punch items addressed within the contract window (usually 30 days).

Owner training session — fixtures, valves, isolation, water-heater operation,
            backflow location + test schedule. Sign attendance.

Submit final O&M manual with all submittal data + warranty info.

Submit final as-builts (paper + PDF) to GC + owner.

Apply for Final Completion + final retention pay app.

Respond to warranty calls per contract response-time requirement.

Document each warranty visit; track cumulative count against budget.

Month 11 walk — pre-warranty-expiration check with owner.

Warranty release at end of period; archive job file.

All fixtures secured + functional (flow, drain, no leaks at supplies + drains).

Lavatory + sink faucet flow within code limits (typically ≤2.2 gpm at 60 psi
            for kitchen, ≤0.5 gpm for public lavatories — verify code edition).

Water-closet flush volume ≤1.28 gpf (1.6 gpf for older grandfathered installations).

Hot-water delivery time — many AHJs check time-to-110°F at farthest fixture.

Trap seals + venting — no double-trapping, no S-traps, all vents tied per IPC Ch 9.

Cleanouts accessible + capped.

Backflow devices with initial test reports posted at the device + on file.

Water heater: T&P relief discharge routed correctly (within 6" of floor or to
            indirect waste), seismic strap, expansion tank where required, combustion air.

Gas: shutoff at each appliance, sediment trap, drip leg if required, vent connector
            secured + supported.

Disinfection certificate on file.

Cross-connection control specialist's report on file with water purveyor.

Punch items are tracked in the companion Punch List XLSX. Best practice:

Self-punch BEFORE the GC walk — find your own deficiencies first.

Photograph each punch item with location reference (room + fixture + view).

Assign each item to a journeyman with a target completion date.

Update daily until cleared.

Submit closed-punch certification to GC weekly during the closeout window.

Final walk should produce ZERO new items — if it doesn't, the self-punch was incomplete.

|  | Substantial Completion | Final Completion |
| --- | --- | --- |
| Trigger | Owner can occupy + use for intended purpose | All punch items cleared + final docs submitted |
| AHJ status | Certificate of Occupancy issued (or T.C.O.) | N/A — already issued |
| Retention | Partial release per contract (often 50%) | Full retention release |
| Warranty start | Warranty period begins (typically) | Continues from substantial |
| LD's | Cease accruing | N/A |
| Lien rights | Don't waive without final docs | Conditional final waiver at full payment |

Provide one (1) hard-copy binder + PDF on USB to the owner. Tab dividers per section:

Cover sheet — project name, address, contractor info, document version + date.

Table of contents.

Plumbing system overview — schematic + system description.

Equipment data sheets — water heaters, booster pumps, sewage ejectors, grease
            interceptors, RPZ / DCV devices.

Approved submittals — every approved submittal in the order of CSI section.

Manufacturer O&M booklets for installed equipment.

Test reports — pressure test log, disinfection certificate, backflow initial
            tests.

As-built drawings (reduced + full-size pocket).

Warranty certificates — contractor warranty + manufacturer warranties.

Recommended maintenance schedule.

Vendor contact list — service tech, fixture supplier, water purveyor.

Emergency procedures — main shutoff locations, gas shutoff, sewer backup contact.

Maintain redlines throughout construction — both rough-in foreman + trim-out foreman.

Capture: actual underground routing + depths, valve locations, BFP locations,
            cleanouts, sleeves, all deviations from contract drawings.

Mark survey markers / coordinates where applicable.

Final as-builts as PDF + printed reduced + full-size in CAD (DWG/DXF) if specified.

Submit per contract — typically 30 days post-substantial completion.

| Standard plumbing warranty | 1 year from substantial completion (verify contract) |
| --- | --- |
| Mfr equipment warranty | Per mfr — typically 1-5 years; transfer registrations to owner |
| Underground-piping extended | Per contract — often 2-10 years on buried sanitary or storm |
| Response-time SLA | Per contract — typical: emergency < 24 hr, non-emergency < 5 business days |
| Owner reports through | Single email + phone in O&M manual; log every call |
| Document each visit | Service ticket + photo + sign-off by owner rep |

| Item | Recipient | Due By | Confirmation Required |
| --- | --- | --- | --- |
| Pressure test log | GC + AHJ | Final inspection | Yes |
| DWV / stack test results | GC + AHJ | Final inspection | Yes |
| Gas pressure test report | GC + AHJ | Pre-gas-meter set | Yes |
| Backflow initial test reports | Water purveyor + AHJ + owner | Within 10 days of testing | Yes |
| Disinfection certificate | AHJ + water purveyor + owner | Pre-occupancy | Yes |
| Final as-built drawings | GC + owner | 30 days post-substantial | Yes |
| O&M manual | Owner | Substantial completion | Yes (signed receipt) |
| Warranty letter | Owner + GC | Substantial completion | Yes |
| Equipment registrations | Manufacturers | Within 60 days of substantial | Receipts retained |
| Final lien waiver | GC + owner | Final payment | Yes (notarized if required) |

Progress waivers — conditional / unconditional per payment. Don't
            sign unconditional waivers until paid in cleared funds.

Substantial-completion partial release — typically half of
            retention at substantial; balance at final.

Final release — conditional final waiver upon receipt of retention.
            Then unconditional final after funds clear.

Notice-of-completion — most states require an NOC to start the
            lien-period clock; track the NOC + your lien deadlines.

Vendor + sub release — collect waivers from your own subs +
            material suppliers before signing your own final.

Missing disinfection certificate — most-common holdup for Certificate of Occupancy.

Backflow initial-test report missing or not submitted to water purveyor.

As-built deviations not captured during rough-in (years-later RFI nightmares).

Warranty registration cards not mailed in.

Unsigned owner training attendance sheet.

Submittal book missing a section (kitchen-equipment plumbing rough often forgotten).

Punch list closed without photo proof — owner rejects without re-trip.

O&M manual missing emergency contacts.

Unconditional waiver signed before payment cleared.

Vendor / sub lien waivers not collected — your final release is blocked.