Pipe Material Selection by System

Joining Methods (Solder / Press / Threaded / Solvent / Crimp / Welded)

Hanger & Support Spacing (IPC 308 / UPC 314)

Pipe Expansion & Thermal Movement

Insulation & Cold-Water Sweating

Sleeves & Firestop at Penetrations

Pressure Testing (IPC 312)

Gas Pressure Testing (IFGC 406)

Disinfection (AWWA C651)

Common Installation Errors

| System | Common Materials | Notes |
| --- | --- | --- |
| Domestic Cold Water | Copper Type L, PEX-A, PEX-B, CPVC | PEX-A best freeze tolerance + flow; copper most expensive but longest life |
| Domestic Hot Water | Copper Type L, PEX-A, PEX-B, CPVC | Verify PEX rating at design temperature; copper at 180°F+ near WH |
| DWV — sanitary + vent | PVC Sch 40, ABS, cast iron service-weight, cast iron no-hub | Cast iron required by some AHJs for fire-rated assemblies + commercial multi-story |
| Storm Drainage | PVC Sch 40, cast iron, HDPE | HDPE for buried site storm; PVC for interior |
| Natural Gas (interior) | Black iron schedule 40, CSST (with arc-bonding) | CSST requires arc-bonding for lightning protection per NFPA 54 |
| Natural Gas (underground) | PE-2406 / 2708 (utility-grade plastic), coated steel | PE requires tracer wire + meter-side transition fitting |
| Compressed Air | Copper Type L, aluminum (e.g. Transair), galvanized steel | NEVER use PVC for compressed air — catastrophic failure mode |
| Medical Gas (per NFPA 99) | ASTM B819 medical-gas copper (Type K or L) | Brazing under nitrogen purge; ASSE 6010 brazer required |
| Hot-Water Heating (hydronic) | Copper Type L, PEX-A with oxygen barrier, black steel | Oxygen-barrier PEX required by most boiler manufacturers |
| Glycol Loops | Copper Type L, black steel, PEX-A with O2 barrier | RPZ required upstream (cross-connection) |

| Method | Material | Key Points |
| --- | --- | --- |
| Solder (sweat) | Copper | Lead-free solder only (≤0.25% Pb, SDWA). Clean + flux + heat evenly + apply solder to joint not flame. Hot work permit + fire watch required. |
| Press fitting | Copper, stainless, carbon | ProPress, Megapress. Calibrated press tool. Mark insertion depth + visually confirm before pressing. No hot work — eliminates fire-watch + permit. |
| Solvent cement | PVC, CPVC, ABS | Primer (purple — required by most AHJs for PVC + CPVC), then cement. Quarter-turn during insertion. Hold per ASTM cure-time table. Verify SDS ventilation. |
| Threaded | Black iron, galvanized, brass | Thread compound or PTFE tape rated for gas service. NEVER tape PVC threads — use Teflon-paste designed for plastic. Don't over-tighten plastic threads. |
| PEX crimp / cinch / expansion | PEX-A, PEX-B | Match the fitting + tool to the brand. Go/no-go gauge after crimp. Expansion fittings (PEX-A only) require expander tool. |
| Welded | Black iron, stainless | Certified welder (AWS QW-461). Pressure-system welding subject to ASME B31.9 where applicable. |
| Brazed (silver) | Medical-gas copper | Nitrogen purge during braze (NFPA 99 5.1.10.5). BCuP or BAg brazing alloy. ASSE 6010 brazer certificate. |
| No-hub coupling | Cast iron DWV | Stainless shield with neoprene gasket + clamps. Torque per manufacturer (typically 60–80 in-lb). Verify torque on every joint. |
| Fusion (heat) | HDPE, polypropylene | Socket / butt fusion with the manufacturer's machine + temperature chart. |

Per IPC 308 / UPC 314. Verify the AHJ-adopted edition + any local amendments.
    Vertical support typically at every story OR 10 feet max — whichever is shorter.

| Material | Pipe Size | Horizontal Spacing | Vertical Spacing |
| --- | --- | --- | --- |
| Copper | 1/2" - 1" | 6 ft | 10 ft / per story |
| Copper | 1-1/4" - 2" | 8 ft | 10 ft / per story |
| Copper | 2-1/2" + | 10 ft | 10 ft / per story |
| CPVC | 1/2" - 1" | 3 ft (hot) / 4 ft (cold) | per story |
| CPVC | 1-1/4" + | 4 ft (hot) / 5 ft (cold) | per story |
| PVC DWV | All sizes | 4 ft (1-1/2" -2") / 4 ft (3"+) — verify code | per story |
| Cast Iron | All sizes | 5 ft maximum AND at every joint | per story + at base |
| PEX | 1/2" - 1" | 32" (per most manufacturers) | per story |
| Black Iron Gas | 1/2" - 1" | 6 ft (horizontal) | per story |
| Black Iron Gas | 1-1/4" + | 10 ft (horizontal) | per story |

Hot lines expand. Failure to accommodate movement bows pipes between hangers, breaks
    fittings, and creates noise complaints in occupied spaces. Use expansion loops, swing
    joints, or expansion compensators on runs >30 ft of hot water.

| Material | Expansion (in / 100 ft / 100°F) | Note |
| --- | --- | --- |
| Copper | 1.1" | Brittle if frozen — bursts on cold runs without insulation |
| CPVC | 4.6" | Significant — design expansion loops on all hot runs |
| PEX-A | 9.0" | Most forgiving — but anchor at fixtures + valves |
| Steel (black iron) | 0.8" | Threads tolerant; welded systems need bellows |
| HDPE | 10.0" | Buried installations rely on soil restraint |

Hot water — IECC 2021 + most state energy codes require insulation
            on all hot-water lines. Thickness varies by pipe size (typically 1" for 1/2"-1"
            and 1-1/2" for larger).

Cold water — sweating control + freeze prevention in
            unconditioned spaces. R-2.5 minimum or per local code.

Recirculation loops — full insulation including return.
            Uninsulated recirc lines are an enormous energy waste.

Vapor barriers — required on cold lines in humid spaces to
            prevent condensation drip.

Joint sealing — overlap joints + seal with PVC tape or vapor-tight
            sealant. Open seams defeat the system.

Every penetration through a rated wall, floor, or ceiling must be firestopped per a
    UL-listed assembly that matches the substrate AND the pipe.

Sleeve sizing — typically 1" larger than pipe OD for thermal movement.
            Larger if floating insulation or vibration.

Floor sleeves — extend 1" above finished floor in wet areas; coordinated
            with finished-floor schedule.

Firestop products — intumescent sealant (3M, Hilti, STI). NEVER
            substitute generic foam or caulk — the AHJ will fail the inspection.

UL listing — match the system number to the assembly. Photograph
            each penetration with the system number visible for closeout.

Cast-iron through firewall — many UL systems require a metal
            collar; don't omit.

| System | Test Pressure | Duration | Pass |
| --- | --- | --- | --- |
| DWV (rough-in) | 10' head water OR 5 psi air | 15 min min | No pressure loss |
| DWV (finish, stack) | Water to top of stack OR 1 psi air | 15 min | No leaks |
| Domestic water (rough) | Working +50 psi, 100 psi min | 15 min | No pressure loss |
| Storm | 10' head water OR 5 psi air | 15 min | No pressure loss |
| Hydronic | Per engineer of record | Per spec | No pressure loss |

| System | Test Pressure | Duration |
| --- | --- | --- |
| 2-psi (typical commercial) | 3 psi minimum, 1-1/2× working | 10 min minimum; longer for larger systems |
| High-pressure (> 14 oz / sq in) | 1-1/2× working, gauged + witnessed | Per IFGC 406 / engineer of record |
| Medical gas (NFPA 99) | Multi-stage per NFPA 99 Ch 5 | Per NFPA 99 — pressure + cross-connection + concentration tests |

Test with inert gas (air or nitrogen). Never use the fuel gas itself for testing.

Calibrated gauge in line with the test pressure range — pressure should fall in
            middle third of gauge scale.

Soap-test every joint. AHJ may witness selected joints.

Document test in Pressure Test Log XLSX.

Domestic water systems must be disinfected before service. Most AHJs require a
    disinfection certificate on file for Certificate of Occupancy.

Method 1 — continuous-feed, 50 mg/L (50 ppm), 24-hour hold.

Method 2 — high-dose, 200 mg/L, 3-hour hold (rarely used commercially).

Flush to ≤1 mg/L residual.

Two bacteriological samples ≥24 hours apart — no coliform.

Submit lab report + chain-of-custody to AHJ + water purveyor.

Tight-grade DWV slopes that result in solids dropout (≥1/4" per ft to 1/2" per ft for >3"; 1/8" per ft minimum <3").

Tape on plastic threads — use paste designed for plastic.

Hot work without permit + fire watch.

RPZ installed without bypass on critical service-entry locations.

Solvent cement applied to wet pipe (rain or condensation) — joint never cures.

PEX run through metal stud without grommet — chafe + leak in 1-3 years.

CPVC under stress at fittings — radius-to-fitting transition cracks the fitting.

Missing trap primer on infrequently-used floor drains — odor + sewer-gas migration.

Combustion air not provided to gas-fired water heater in confined-space closet.

Pressure test with water in winter (freezes in unheated areas).