This Site-Specific Plumbing Plan ("SSPP") is the plumbing contractor's project-specific
        compliance roadmap covering AHJ coordination, the inspection sequence, cross-connection
        control, hydrostatic and pressure testing, confined-space work, trenching, hot work,
        hazmat encountered during demolition, and multi-trade coordination. Tailor every variable
        to the actual project, walk it with the project superintendent + AHJ plumbing inspector
        before underground rough-in begins, and sign at Section 16. Keep a copy in the jobsite
        trailer with the permit, plumbing drawings, and the Universal Sub Suite's Daily Field
        Report binder. The OSHA Multi-Employer Citation Policy applies — the controlling
        contractor and the plumbing contractor are jointly citable for site-specific violations.

Section 1 — Parties & Project Identification

Section 2 — Permits, AHJ & Code Edition

Section 3 — Inspection Sequence (UG / Rough / Top-Out / Final)

Section 4 — Plumbing Scope of Work

Section 5 — Cross-Connection Control Plan

Section 6 — Hydrostatic & Pressure Testing

Section 7 — Disinfection of Potable Water (AWWA C651)

Section 8 — Excavation & Trenching (Subpart P)

Section 9 — Confined-Space Entry (1910.146 / 1926 Subpart AA)

Section 10 — Hot Work (Welding, Soldering, Sweating)

Section 11 — Hazmat Encountered (Asbestos / Lead / Mold)

Section 12 — Multi-Trade Coordination (MEP)

Section 13 — Occupied-Building / ICRA Considerations

Section 14 — Emergency Response

Section 15 — Stop-Work Triggers

Section 16 — Signatures

| Project Name | [Project Name] |
| --- | --- |
| Project Address | [Address, City, State ZIP] |
| Owner | [Owner Legal Name + Rep + Phone] |
| General Contractor (controlling) | [GC Legal Name + Project Manager + Phone] |
| Architect | [Architect Firm + Project Architect] |
| Plumbing Engineer of Record | [MEP Firm + Engineer-of-Record stamp] |
| Plumbing Contractor | [Plumbing Contractor Legal Name] |
| Plumbing State License # | [License # + Master Plumber name] |
| Plumbing Superintendent | [Name + Phone — primary site contact] |
| Plumbing Foreman | [Name + Phone] |
| Estimated Start Date | [Date] |
| Estimated Substantial Completion | [Date] |
| Project Type | [New Construction / Renovation / Tenant Fit-out / Adaptive Reuse] |
| Building Occupancy Group | [A / B / E / F / H / I / M / R / S / U — IBC Chapter 3] |
| Construction Type | [I-A / I-B / II-A / II-B / III-A / III-B / IV / V-A / V-B — IBC Chapter 6] |

| Plumbing Permit # | [Permit number + issue date] |
| --- | --- |
| AHJ — Building Department | [Jurisdiction name + phone + portal URL] |
| AHJ — Plumbing Inspector | [Inspector name + cell + email] |
| Inspection Request Method | [Online portal / phone / email — and required lead time] |
| Adopted Plumbing Code | [IPC 2024 / UPC 2024 / NSPC + local amendments] |
| Adopted Fuel Gas Code | [IFGC 2024 / NFPA 54] |
| Local Cross-Connection Authority | [Water purveyor + cross-connection specialist] |
| Water Purveyor | [Utility name + meter / tap fee account #] |
| Sanitary Sewer Authority | [Utility name + connection-permit account #] |
| Storm Sewer Authority | [Same or different — name + account] |

The following sequence is typical for new commercial construction. Confirm with the
    AHJ plumbing inspector at the pre-construction meeting. No subsequent work covers
    inspected work until the inspector signs off.

| Inspection | Trigger | What gets inspected |
| --- | --- | --- |
| Underground / In-Slab | Before backfill / slab pour | Sanitary, storm, and water lines under slab; cleanouts; trap-primer rough; sleeves; hydrostatic / air test held during inspection |
| Above-Slab Rough-In | Before drywall | DWV stacks + vents + horizontal branches; domestic water risers + branches; gas lines; pressure tests held; hangers + supports per IPC 308; firestop seals visible |
| Top-Out / Stack Test | DWV system pressurized for final inspection | Stack tested to top fitting (10 ft head OR 5 psi air); no leaks; vents per IPC Chapter 9 sizing |
| Gas Pressure Test | Before connection of any appliance | System held at test pressure per IFGC 406 (typically 3 psi for 10 min minimum on 2-psi systems); inspector witnesses |
| Backflow Initial Test | After installation, before placing in service | Certified tester (state-licensed) tests each RPZ / DCV / PVB per ASSE/CSA; submits report to water purveyor + AHJ |
| Water-Heater / Boiler | Before insulation / drywall over T&P discharge piping | T&P relief discharge routed per IPC 504.6; seismic strap (high-zone); combustion air per IFGC Ch 9; vent connector |
| Final | All fixtures installed + system commissioned | Fixtures secure + functional; faucets meet flow limits; hot-water delivery time; trap seals; backflow report on file; disinfection certificate on file |

List the CSI Division 22 scope items this contract covers. Cross-reference Division 23
    (mechanical) and Division 26 (electrical) for shared scope items. Mark each as
    BY US, BY OTHERS, or SHARED.

| CSI Code | System | Scope |
| --- | --- | --- |
| 22 11 | Domestic Water Distribution | BY US / BY OTHERS / SHARED — describe |
| 22 13 | Sanitary Sewerage (interior) | [scope] |
| 22 14 | Storm Drainage (interior) | [scope] |
| 22 33-35 | Water Heaters / Heat Exchangers | [scope — note IFGC vent install boundary] |
| 22 42-47 | Commercial Plumbing Fixtures | [scope] |
| 22 67 | Natural-Gas Piping (interior) | [scope — note boundary with utility] |
| 22 60-63 | Medical / Lab Gas (if applicable) | [N/A or scope] |
| 23 21 | Hydronic Piping (cross-ref to mechanical) | [typically BY OTHERS — confirm] |
| 21 13 | Fire-Suppression Sprinklers | [BY OTHERS — separate trade] |
| 33 10 | Site Utility — Water Service | [BY US to building / BY OTHERS in ROW] |
| 33 30 | Site Utility — Sanitary Sewer | [BY US to ROW / BY OTHERS] |
| 31 23 | Excavation & Backfill | [BY US / SHARED with site contractor] |

Every potable-water system has cross-connection hazards. The contractor must identify
    each, select the correct backflow-prevention device, and arrange initial + annual testing
    by a state-licensed cross-connection control specialist.

| Hazard Level | Definition | Required Device |
| --- | --- | --- |
| High | Contains substances that, if backflowed, would cause illness, death, or other serious harm (sewage, chemicals, processed water) | RPZ (Reduced-Pressure-Zone Principle Backflow Preventer) — ASSE 1013 |
| Low | Contains substances objectionable but non-toxic (food, beverage) | DCV (Double Check Valve Assembly) — ASSE 1015 |
| Air-gap acceptable | Direct discharge with air gap of 2× pipe diameter or 1 inch, whichever larger | Physical air gap — IPC 608.13.1 |

Building water service entry — RPZ or DCV per water purveyor's policy. In most modern jurisdictions, commercial buildings require RPZ at the meter.

Boilers / hydronic systems — RPZ (high hazard — chemicals/glycol).

Cooling-tower make-up — RPZ (high hazard — biocides + scale inhibitors).

Lawn-irrigation system — PVB (Pressure-Vacuum Breaker) ASSE 1020 or DCV depending on chemical injection.

Fire-protection sprinkler — DCV without chemical additives; RPZ with chemical additives or recycled water.

Carbonators / soda machines — ASSE 1022 stainless-steel double-check; coordinate with foodservice vendor.

Wall hydrants / hose bibbs — integral vacuum breaker per IPC 608.15.4.1.

Hand-held showers / kitchen sprayers — integral backflow preventer per fixture standard.

All plumbing systems require pressure testing before being concealed and again at
    completion. Performance below is the contractor's responsibility; the inspector witnesses
    selected tests.

| System | Test Pressure | Duration | Reference |
| --- | --- | --- | --- |
| DWV (rough-in) | 10-foot head of water OR 5 psi air | 15 min minimum — no pressure loss | IPC 312.2 / UPC 712 |
| DWV (finish, stack test) | Water to top of stack OR 1 psi air | 15 min — no leaks | IPC 312.4 |
| Domestic water (rough-in) | Working pressure +50 psi, minimum 100 psi | 15 min — no pressure loss | IPC 312.5 |
| Domestic water (finish) | Working pressure | Verify by fixture operation | IPC 312.5 |
| Natural gas (2-psi) | 3 psi minimum, 1-1/2× working pressure | 10 min minimum (longer for larger systems) | IFGC 406.4 / NFPA 54 |
| Natural gas (high-pressure) | Per engineer of record + utility — typically 1-1/2× working | Per IFGC 406 / utility requirement | IFGC 406 |
| Storm | 10-foot head of water OR 5 psi air | 15 min — no pressure loss | IPC 1108 |
| Medical gas (if applicable) | Per NFPA 99 — multiple-stage test | Per NFPA 99 testing protocol | NFPA 99 Ch 5 |

Verify all openings capped + test caps rated for the test pressure.

For air tests over 5 psi: clear personnel from the test radius (failures can launch fittings — see warning below). Tape barricade.

Apply test pressure with calibrated gauge. Record start time + pressure.

Soap or leak-detect every joint visually. Look + listen.

At end of duration, record finish pressure. No drop = pass.

Document on the Pressure Test Log XLSX. Photo the gauge + system at start + finish.

Domestic water piping must be disinfected before being placed in service.
    Most AHJs require a disinfection report on file before issuing the Certificate of
    Occupancy.

Flush the system thoroughly to remove debris.

Introduce chlorine to achieve 50 mg/L (50 ppm) free chlorine residual at the
            farthest fixture. Verify with a DPD-1 test strip or colorimeter.

Hold for 24 hours minimum.

Test all dead-ends + outlets for ≥10 mg/L residual at end of hold.

Flush the entire system until residual drops to ambient (≤1.0 mg/L typically).

Submit two bacteriological samples taken 24 hours apart to an accredited lab.
            Both must show no coliform OR per-jurisdiction equivalent.

Submit the lab report + chain-of-custody to the AHJ + water purveyor.

Underground plumbing work involves trenching that triggers OSHA 1926 Subpart P. The
    most-cited deaths are cave-ins; the most-cited violation is failure to identify a Competent
    Person.

Call 811 minimum 2 business days before digging — locate all utilities.

Document the locate ticket + paint markings before breaking ground. Photograph.

Designate a Competent Person for each shift — trained per 1926.651(k).

Pre-plan the soil classification (Type A / B / C per 1926 App A).

Select the protective system (sloping / shoring / shielding) appropriate to depth + soil.

Confirm spoil pile ≥2 ft from edge of excavation.

Provide ladders or steps in any trench ≥4 ft, max 25 ft of lateral travel.

| Depth | Soil Type A (cohesive, hard clay) | Soil Type B (cohesive, sandy clay) | Soil Type C (granular, water-saturated) |
| --- | --- | --- | --- |
| 0 – 4 ft | No system required if competent person evaluates | No system if competent person evaluates | No system if competent person evaluates |
| 4 – 5 ft | Slope 3/4:1 or shore | Slope 1:1 or shore | Slope 1-1/2:1 or shield |
| 5 – 20 ft | Slope 3/4:1 or engineered shoring | Slope 1:1 or engineered shoring/shield | Slope 1-1/2:1 or engineered shield (trench box) |
| > 20 ft | Engineered system required — registered PE design |  |  |

Plumbing work frequently encounters permit-required confined spaces: existing sanitary
    or storm manholes, sumps, sewage ejector pits, tanks, boiler rooms with limited egress.
    Document the program below for every entry.

Identify the space. Is it large enough to bodily enter, with limited or restricted
            means of entry/exit, NOT designed for continuous occupancy? → confined space.

Does it have ANY hazard (atmospheric, engulfment, configuration-trap,
            electrical, mechanical)? → permit-required confined space (PRCS).

If PRCS: STOP. Implement the permit program.

Written entry permit signed by the Entry Supervisor before any entry.

Atmospheric testing in this order: oxygen → flammable gases → toxics.
            Re-test continuously while occupied (or every 15 min minimum).

Authorized entrant(s), attendant(s) outside, and entry supervisor — all trained per
            1910.146(g) within the prior 12 months.

Communication system between entrant and attendant maintained throughout.

Retrieval system (full-body harness + retrieval line + mechanical advantage)
            unless retrieval would increase risk.

Rescue services available — verify response time + capability before entry.

Lock-out / tag-out of all energy sources that could enter the space.

Most plumbing operations include some hot work — soldering copper, sweating Pro-Press
    in tight areas, gas-piping welding, brazing of medical gas. The General Contractor's
    site-specific Hot Work Permit program controls.

Obtain a Hot Work Permit from the GC before each shift. Don't pre-pull or rubber-stamp.

Clear 35 ft of combustibles or cover with welding blankets / FR tarps. Sweep up dust + lint within the radius.

Fire watch designated for the duration of hot work PLUS a minimum 30-min cool-down (60 min on some AHJ amendments).

Fire extinguisher (Class A + B + C) within 10 ft of the work.

Suspend hot work and notify GC if smoke alarms are disabled and not re-armed within 30 min of work completion.

Brazing of medical gas: NITROGEN PURGE during the braze per NFPA 99 5.1.10.5. No exceptions.

Outdoor wind: cease hot work above 15 mph wind or during dust events.

Renovations and tenant fit-outs in buildings constructed before approximately 1980 may
    expose workers to asbestos pipe insulation, lead solder, lead-based paint disturbance,
    and mold growth in damp envelopes. Treat each as a stop-work item until characterized.

Common in pre-1980 commercial pipe insulation (white plaster-like wrap on hot-water
            and boiler-feed lines).

STOP work and isolate the area. Notify the GC + owner immediately.

Survey by a state-licensed asbestos inspector before any disturbance.

Removal by a licensed abatement contractor. The plumbing contractor does NOT remove
            ACM unless specifically licensed.

Federal: 29 CFR 1926.1101 (construction) + 40 CFR Part 61 Subpart M (NESHAP).

Pre-1986 domestic water solder was 50% lead. Replacement service lines + soldered
            connections must be lead-free per the 2014 SDWA amendment (≤0.25% lead weighted
            average).

Renovation in pre-1978 buildings that disturb painted surfaces triggers EPA RRP
            (Renovation, Repair, and Painting) requirements — certified renovator on site.

Lead solder cutout: HEPA vacuum the work area, contain dust, and document chain of
            custody for disposal.

Wet drywall + insulation around leaking pipes can incubate mold within 48–72 hours.

Containment + remediation per IICRC S520 or local AHJ standard before plumbing
            work resumes in the affected area.

Plumbing rough-in conflicts with HVAC ducts, electrical conduit, fire-protection mains,
    and structural framing more than any other trade. Resolve before installation.

Coordination drawings — overlay plumbing rough on the M / E / FP /
            S drawings. Identify clashes before pulling permits.

BIM coordination meetings on projects using BIM 360 / Navisworks —
            attend every cycle. Document clash resolutions in writing.

Slab and wall openings — coordinate with concrete + framing
            contractors. Provide sleeve schedule, openings packet, embed locations 7–10 days
            ahead of pour.

Hangers and supports — verify structural attachment points are
            approved by the EOR. No drilling into post-tensioned slabs without scan + EOR sign-off.

Firestop coordination — UL-listed assemblies for each penetration
            type. Coordinate with the firestop sub on inspection witness.

Above-ceiling priority — typical commercial: structure → gravity
            (storm, sanitary) → HVAC ducts → sprinkler mains → domestic water → electrical →
            communications. Confirm at coordination meeting.

Tenant fit-outs, hospital renovations, and educational-facility work often proceed
    with occupants in adjacent areas. Adjust the plan accordingly.

Healthcare ICRA tier — coordinate with the infection-control
            preventionist. Tier III or IV work requires negative-pressure containment + HEPA.

Water-shutdown notice — give occupants minimum 48-hour written
            notice for any planned water shutdown. Schedule for off-hours where feasible.

Sewer-cap protocols — never leave an open DWV line uncapped; sewer
            gases (H2S, methane) accumulate in inhabited spaces within hours.

Noise + odor — solder + flux smoke, no-hub coupling work, and gas
            purges all create odors. Coordinate ventilation + occupant notice.

After-hours work — verify janitorial schedule + alarm systems.
            Document badge access + after-hours sign-in procedure.

| Site First-Aid Station | [Location + supplies + AED if equipped] |
| --- | --- |
| Nearest Hospital | [Name + address + ER phone + drive time] |
| Site Emergency Contact | [GC superintendent + cell] |
| Owner Emergency Contact | [Owner's facilities rep] |
| Water Shutoff — Main | [Location + valve handle + responsible person] |
| Gas Shutoff — Main | [Location + valve + responsible person] |
| Sewer Backup Response | [Vendor + 24-hr phone] |
| Hazmat / Spill Contact | [Vendor + 24-hr phone + EPA NRC 800-424-8802] |
| 911 Address Reciprocity | [How to direct EMS to site — gate codes, exact entry, posted address] |

Any worker on this project has Stop-Work Authority for the following conditions.
    Document the stop, notify the plumbing superintendent + GC, and do not resume until
    documented resolution.

Suspected asbestos, lead-based paint, or mold disturbance.

Confined-space entry without a valid permit + atmospheric test.

Trench cave-in risk — soil change, water intrusion, equipment vibration.

Cross-connection identified that was not previously documented.

Pressure-test failure that cannot be diagnosed within reasonable time.

Energized utility encountered unexpectedly (live water main, live gas).

Code-edition conflict between drawings and AHJ adopted code.

Backflow device discharging continuously (failed RPZ or test cock open).

Sewage spill exceeding 5 gallons indoors or any spill outdoors.

Worker injury exceeding first-aid level.

The undersigned have reviewed this Site-Specific Plumbing Plan and concur with the
    procedures, responsibilities, and stop-work triggers documented herein.

Revision history: log each substantive change with date, page reference, and signer.
        Post the current version at the jobsite trailer. Older versions to the project closeout
        binder.